## Boiler Oil
Fuel Oil-Fired Boilers & Heaters | [7 empty] | Heating Value of #2 & Distillate | 140 | MMBtu/1,000 gal |  |  |  | Formula for Fuel Usage, if changed.
Equipment Details | [7 empty] | Heating Value of #4, #5, #6 Oils | 150 | MMBtu/1,000 gal |  |  | 178.5714 | =IF($C$7="Distillate",$B$3/$K$1*1000,$B$3/$K$2*1000)
Rating | 25 | MMBtu/hour
Operational Hours | 8760 | hours/year |  |  |  | NOx | Size | Table 1.3-1 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
Boiler Type | Industrial | [5 empty] | >100 MMBtu/hr | #6, Normal Firing | 47 | 0.31333 | 7.8333 | 34.31
Use | Manufacturing, etc.
Firing Type | Normal | [5 empty] | >100 MMBtu/hr | #6, Normal Firing, Low Nox burner | 40 | 0.26667 | 6.6667 | 29.2
Fuel Oil Grade Number | 2 | Distillate |  |  |  |  | >100 MMBtu/hr | #6, Tangential Firing | 32 | 0.21333 | 5.3333 | 23.36
Sulfur Content | 0.0015 | % or 15 ppm |  |  |  |  | >100 MMBtu/hr | #6, Tangential Firing, Low Nox burner | 26 | 0.17333 | 4.3333 | 18.98
Fuel Usage | 178.5714 | gallons/hour |  |  |  |  | >100 MMBtu/hr | #5, Normal Firing | 47 | 0.31333 | 7.8333 | 34.31
[7 empty] | >100 MMBtu/hr | #5, Tangential Firing | 32 | 0.21333 | 5.3333 | 23.36
Criteria Pollutant | Emission Factor (lb/10^3 gal) |  | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference |  | >100 MMBtu/hr | #4, Normal Firing | 47 | 0.31333 | 7.8333 | 34.31
NOX |  | 20 | 3.5714 | 15.6429 | AP-42 Table 1.3-1 |  | >100 MMBtu/hr | #4, Tangential Firing | 32 | 0.21333 | 5.3333 | 23.36
CO |  | 5 | 0.89286 | 3.9107 |  |  | >100 MMBtu/hr | #2, Normal Firing | 24 | 0.17143 | 4.2857 | 18.7714
PM10 |  | 2.3 | 0.41071 | 1.7989 | AP-42 Tables 1.3-2, 4, 5, 6, & 7 |  | >100 MMBtu/hr | #2, Normal Firing, Low Nox/FGR | 10 | 0.071429 | 1.7857 | 7.8214
PM2.5 |  | 1.55 | 0.27679 | 1.2123 |  |  | <100 MMBtu/hr | #6, Normal Firing | 55 | 0.36667 | 9.1667 | 40.15
SO2 |  | 0.213 | 0.038036 | 0.1666 | AP-42 Table 1.3-1 |  | <100 MMBtu/hr | #5, Normal Firing | 55 | 0.36667 | 9.1667 | 40.15
VOC |  | 0.2 | 0.035714 | 0.15643 | AP-42 Table 1.3-3 |  | <100 MMBtu/hr | #4, Normal Firing | 20 | 0.13333 | 3.3333 | 14.6
Lead |  | 0.00126 | 0.000225 | 0.0009855 | AP-42 Table 1.3-11 |  | <100 MMBtu/hr | Distillate, Normal | 20 | 0.14286 | 3.5714 | 15.6429 | Match
HAP |  |  | 0.014138 | 0.061925 | See Below |  | <100 MMBtu/hr | Residential Furnace | 18 | 0.12857 | 3.2143 | 14.0786
Green House Gas Pollutant | Global Warming Potential | Emission Factor (lb/10^3 gal) | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | CO | Size | Table 1.3-1 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
CO2 (mass basis) | 1 | 22300 | 3982.1429 | 17441.7857 | AP-42 Tables 1.3-3, 1.3-8, 1.3-12, & Table A-1 to Subpart A of Part 98 |  | >100 MMBtu/hr | #6, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
Methane (mass basis) | 25 | 0.052 | 0.0092857 | 0.040671 |  |  | >100 MMBtu/hr | #6, Normal Firing, Low Nox burner | 5 | 0.033333 | 0.83333 | 3.65
N2O (mass basis) | 298 | 0.26 | 0.046429 | 0.20336 |  |  | >100 MMBtu/hr | #6, Tangential Firing | 5 | 0.033333 | 0.83333 | 3.65
CO2e |  |  |  | 17503.4029 |  |  | >100 MMBtu/hr | #6, Tangential Firing, Low Nox burner | 5 | 0.033333 | 0.83333 | 3.65
[7 empty] | >100 MMBtu/hr | #5, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
Hazardous Air Pollutant | Emission Factor (lb/10^3 gal) |  | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference |  | >100 MMBtu/hr | #5, Tangential Firing | 5 | 0.033333 | 0.83333 | 3.65
Polycyclic Organic Matter |  | 0.0033 | 0.00058929 | 0.0025811 | AP-42 Table 1.3-8 |  | >100 MMBtu/hr | #4, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
Formaldehyde |  | 0.061 | 0.010893 | 0.047711 |  |  | >100 MMBtu/hr | #4, Tangential Firing | 5 | 0.033333 | 0.83333 | 3.65
Benzene |  | 0.000214 | 3.8214e-05 | 0.00016738 | AP-42 Table 1.3-9 |  | >100 MMBtu/hr | #2, Normal Firing | 5 | 0.035714 | 0.89286 | 3.9107 | Match
Ethylbenzene |  | 6.36e-05 | 1.1357e-05 | 4.9744e-05 |  |  | >100 MMBtu/hr | #2, Normal Firing, Low Nox/FGR | 5 | 0.035714 | 0.89286 | 3.9107 | Match
Naphthalene |  | 0.00113 | 0.00020179 | 0.00088382 |  |  | <100 MMBtu/hr | #6, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
1,1,1-Trichloroethane |  | 0.000236 | 4.2143e-05 | 0.00018459 |  |  | <100 MMBtu/hr | #5, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
Toluene |  | 0.0062 | 0.0011071 | 0.0048493 |  |  | <100 MMBtu/hr | #4, Normal Firing | 5 | 0.033333 | 0.83333 | 3.65
o-Xylene |  | 0.000109 | 1.9464e-05 | 8.5254e-05 |  |  | <100 MMBtu/hr | Distillate, Normal | 5 | 0.035714 | 0.89286 | 3.9107 | Match
Acenaphthene |  | 2.11e-05 | 3.7679e-06 | 1.6503e-05 |  |  | <100 MMBtu/hr | Residential Furnace | 5 | 0.035714 | 0.89286 | 3.9107 | Match
Acenaphthylene |  | 2.53e-07 | 4.5179e-08 | 1.9788e-07
Anthracene |  | 1.22e-06 | 2.1786e-07 | 9.5421e-07 |  |  |  |  | EF x S | Actual
Benz(a)anthracene |  | 4.01e-06 | 7.1607e-07 | 3.1364e-06 |  | SO2 | Size | Table 1.3-1 | lb/10^3 gal | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
Benzo(b,k)fluoranthene |  | 1.48e-06 | 2.6429e-07 | 1.1576e-06 |  |  | >100 MMBtu/hr | #6, Normal Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Benzo(g,h,i)perylene |  | 2.26e-06 | 4.0357e-07 | 1.7676e-06 |  |  | >100 MMBtu/hr | #6, Normal Firing, Low Nox burner | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Chrysene |  | 2.38e-06 | 4.25e-07 | 1.8615e-06 |  |  | >100 MMBtu/hr | #6, Tangential Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Dibenzo(a,h)anthracene |  | 1.67e-06 | 2.9821e-07 | 1.3062e-06 |  |  | >100 MMBtu/hr | #6, Tangential Firing, Low Nox burner | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Fluoranthene |  | 4.84e-06 | 8.6429e-07 | 3.7856e-06 |  |  | >100 MMBtu/hr | #5, Normal Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Fluorene |  | 4.47e-06 | 7.9821e-07 | 3.4962e-06 |  |  | >100 MMBtu/hr | #5, Tangential Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Indeno(1,2,3-cd)pyrene |  | 2.14e-06 | 3.8214e-07 | 1.6738e-06 |  |  | >100 MMBtu/hr | #4, Normal Firing | 150 | 0.225 | 0.0015 | 0.0375 | 0.16425
Phenanathrene |  | 1.05e-05 | 1.875e-06 | 8.2125e-06 |  |  | >100 MMBtu/hr | #4, Tangential Firing | 150 | 0.225 | 0.0015 | 0.0375 | 0.16425
Pyrene |  | 4.25e-06 | 7.5893e-07 | 3.3241e-06 |  |  | >100 MMBtu/hr | #2, Normal Firing | 142 | 0.213 | 0.0015214 | 0.038036 | 0.1666 | Match
OCDD |  | 3.1e-09 | 5.5357e-10 | 2.4246e-09 |  |  | >100 MMBtu/hr | #2, Normal Firing, Low Nox/FGR | 142 | 0.213 | 0.0015214 | 0.038036 | 0.1666 | Match
[5 empty] | AP-42 Table 1.3-10, & Table 1.3-11 (Some HAP do not popluate based on the fuel type selected. AP-42 does not list certain HAP for certain fuel types.) |  | <100 MMBtu/hr | #6, Normal Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Arsenic |  | 0.00056 | 0.0001 | 0.000438 |  |  | <100 MMBtu/hr | #5, Normal Firing | 157 | 0.2355 | 0.00157 | 0.03925 | 0.17191
Beryllium |  | 0.00042 | 7.5e-05 | 0.0003285 |  |  | <100 MMBtu/hr | #4, Normal Firing | 150 | 0.225 | 0.0015 | 0.0375 | 0.16425
Cadmium |  | 0.00042 | 7.5e-05 | 0.0003285 |  |  | <100 MMBtu/hr | Distillate, Normal | 142 | 0.213 | 0.0015214 | 0.038036 | 0.1666 | Match
Chromium |  | 0.00042 | 7.5e-05 | 0.0003285 |  |  | <100 MMBtu/hr | Residential Furnace | 142 | 0.213 | 0.0015214 | 0.038036 | 0.1666 | Match
[6 empty] | PM (cond) | Size | Table 1.3-2 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year
Manganese |  | 0.00084 | 0.00015 | 0.000657 |  |  |  | #2 Oil | 1.3 | 0.0092857 | 0.23214 | 1.0168
Mercury |  | 0.00042 | 7.5e-05 | 0.0003285 |  |  |  | #6 Oil | 1.5 | 0.01 | 0.25 | 1.095
Nickel |  | 0.00042 | 7.5e-05 | 0.0003285
Selenium |  | 0.0021 | 0.000375 | 0.0016425 |  |  |  |  | EF x A | Actual |  | Filterable PM10 |  | Total PM10
[6 empty] | PM10 | Type | Table 1.3-4, 1.3-5, 1.3-6, 1.3-7 | lb/10^3 gal | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | lb/hr | Ton/year | Check
[7 empty] | Utility | #6, A = 1.12(S) + 0.37 | 5.9 | 2.1929 | 0.014619 | 0.36549 | 1.6008 | 0.61549 | 2.6958
[7 empty] | Utility | #5 A = 1.2 | 5.9 | 7.08 | 0.0472 | 1.18 | 5.1684 | 1.43 | 6.2634
[7 empty] | Utility | #4 A = 0.84 | 5.9 | 4.956 | 0.03304 | 0.826 | 3.6179 | 1.076 | 4.7129
[7 empty] | Industrial | #6, A = 1.12(S) + 0.37 | 7.17 | 2.6529 | 0.017686 | 0.44215 | 1.9366 | 0.69215 | 3.0316
[7 empty] | Industrial | #5 A = 1.2 | 7.17 | 8.604 | 0.05736 | 1.434 | 6.2809 | 1.684 | 7.3759
[7 empty] | Industrial | #4 A = 0.84 | 7.17 | 6.0228 | 0.040152 | 1.0038 | 4.3966 | 1.2538 | 5.4916
[7 empty] | Industrial | Distillate (#1 & #2) |  | 1 | 0.0071429 | 0.17857 | 0.78214 | 0.41071 | 1.7989
[7 empty] | Commercial | #6, A = 1.12(S) + 0.37 | 5.17 | 1.9129 | 0.012753 | 0.31882 | 1.3964 | 0.56882 | 2.4914
[7 empty] | Commercial | #5 A = 1.2 | 5.17 | 6.204 | 0.04136 | 1.034 | 4.5289 | 1.284 | 5.6239
[7 empty] | Commercial | #4 A = 0.84 | 5.17 | 4.3428 | 0.028952 | 0.7238 | 3.1702 | 0.9738 | 4.2652
[7 empty] | Commercial | Distillate (#1 & #2) |  | 1.08 | 0.0077143 | 0.19286 | 0.84471 | 0.425 | 1.8615
[9 empty] | EF x A | Actual |  | Filterable PM10 |  | Total PM10
[6 empty] | PM2.5 | Type | Table 1.3-4, 1.3-5, 1.3-6, 1.3-7 | lb/10^3 gal | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | lb/hr | Ton/year | Check
[7 empty] | Utility | #6, A = 1.12(S) + 0.37 | 4.3 | 121.991 | 0.81327 | 20.3318 | 89.0534 | 20.5818 | 90.1484
[7 empty] | Utility | #5 A = 1.2 | 4.3 | 5.16 | 0.0344 | 0.86 | 3.7668 | 1.11 | 4.8618
[7 empty] | Utility | #4 A = 0.84 | 4.3 | 3.612 | 0.02408 | 0.602 | 2.6368 | 0.852 | 3.7318
[7 empty] | Industrial | #6, A = 1.12(S) + 0.37 | 4.67 | 1.7279 | 0.011519 | 0.28798 | 1.2614 | 0.53798 | 2.3564
[7 empty] | Industrial | #5 A = 1.2 | 4.67 | 5.604 | 0.03736 | 0.934 | 4.0909 | 1.184 | 5.1859
[7 empty] | Industrial | #4 A = 0.84 | 4.67 | 3.9228 | 0.026152 | 0.6538 | 2.8636 | 0.9038 | 3.9586
[7 empty] | Industrial | Distillate (#1 & #2) |  | 0.25 | 0.0017857 | 0.044643 | 0.19554 | 0.27679 | 1.2123 | Match
[7 empty] | Commercial | #6, A = 1.12(S) + 0.37 | 1.92 | 0.7104 | 0.004736 | 0.1184 | 0.51859 | 0.3684 | 1.6136
[7 empty] | Commercial | #5 A = 1.2 | 1.92 | 2.304 | 0.01536 | 0.384 | 1.6819 | 0.634 | 2.7769
[7 empty] | Commercial | #4 A = 0.84 | 1.92 | 1.6128 | 0.010752 | 0.2688 | 1.1773 | 0.5188 | 2.2723
[7 empty] | Commercial | #2 A = 0.24 |  | 0.83 | 0.0059286 | 0.14821 | 0.64918 | 0.38036 | 1.666
[6 empty] | VOC | Size | Table 1.3-3 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[7 empty] | Utility | #6, Normal Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Utility | #6, Tangential Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Utility | #5, Normal Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Utility | #5, Tangential Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Utility | #4, Normal Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Utility | #4, Tangential Firing | 0.76 | 0.0050667 | 0.12667 | 0.5548
[7 empty] | Industrial | #6, Normal Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[7 empty] | Industrial | #5, Normal Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[7 empty] | Industrial | Distillate, Normal | 0.2 | 0.0014286 | 0.035714 | 0.15643 | Match
[7 empty] | Industrial | #4, Normal Firing | 0.2 | 0.0013333 | 0.033333 | 0.146
[7 empty] | Comercial | #6, Normal Firing | 1.13 | 0.0075333 | 0.18833 | 0.8249
[7 empty] | Comercial | #5, Normal Firing | 1.13 | 0.0075333 | 0.18833 | 0.8249
[7 empty] | Comercial | Distillate, Normal | 0.34 | 0.0024286 | 0.060714 | 0.26593
[7 empty] | Comercial | #4, Normal Firing | 0.34 | 0.0022667 | 0.056667 | 0.2482
[7 empty] | Residential | Residential Furnace | 0.713 | 0.0050929 | 0.12732 | 0.55767
[6 empty] | Methane | Size | Table 1.3-3 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[6 empty] | 25 | Utility | #6, Normal Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Utility | #6, Tangential Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Utility | #5, Normal Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Utility | #5, Tangential Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Utility | #4, Normal Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Utility | #4, Tangential Firing | 0.28 | 0.0018667 | 0.046667 | 0.2044
[6 empty] | 25 | Industrial | #6, Normal Firing | 1 | 0.0066667 | 0.16667 | 0.73
[6 empty] | 25 | Industrial | #5, Normal Firing | 1 | 0.0066667 | 0.16667 | 0.73
[6 empty] | 25 | Industrial | Distillate, Normal | 0.052 | 0.00037143 | 0.0092857 | 0.040671 | Match
[6 empty] | 25 | Industrial | #4, Normal Firing | 0.052 | 0.00034667 | 0.0086667 | 0.03796
[6 empty] | 25 | Comercial | #6, Normal Firing | 0.475 | 0.0031667 | 0.079167 | 0.34675
[6 empty] | 25 | Comercial | #5, Normal Firing | 0.475 | 0.0031667 | 0.079167 | 0.34675
[6 empty] | 25 | Comercial | Distillate, Normal | 0.216 | 0.0015429 | 0.038571 | 0.16894
[6 empty] | 25 | Comercial | #4, Normal Firing | 0.216 | 0.00144 | 0.036 | 0.15768
[6 empty] | 25 | Residential | Residential Furnace | 1.78 | 0.012714 | 0.31786 | 1.3922
[6 empty] | N2O | Size | Table 1.3-8 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[6 empty] | 298 | All | #6, Normal Firing | 0.53 | 0.0035333 | 0.088333 | 0.3869
[6 empty] | 298 | All | Distillate, Normal | 0.26 | 0.0018571 | 0.046429 | 0.20336 | Match
[6 empty] | 298 | All | Residential Furnace | 0.05 | 0.00035714 | 0.0089286 | 0.039107
[6 empty] | CO2 | Size | Table 1.3-12 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[6 empty] | 1 | All | #1 (Kerosene) | 21500 | 153.5714 | 3839.2857 | 16816.0714
[6 empty] | 1 | All | #2 | 22300 | 159.2857 | 3982.1429 | 17441.7857 | Match
[6 empty] | 1 | All | Low Sulfur #6 | 25000 | 166.6667 | 4166.6667 | 18250
[6 empty] | 1 | All | High Sulfur #6 | 24400 | 162.6667 | 4066.6667 | 17812
[9 empty] | CO2 |  | Methane |  | N2O |  | Total
[6 empty] | CO2e | Size | Table 1.3-3 & 1.3-8 | lb/hr | Ton/year | lb/hr | Ton/year | lb/hr | Ton/year | lb/hr | Ton/year | Check
[7 empty] | Utility | #6, Normal Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Utility | #6, Tangential Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Utility | #5, Normal Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Utility | #5, Tangential Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Utility | #4, Normal Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Utility | #4, Tangential Firing | 4166.6667 | 18250 | 1.1667 | 5.11 | 26.3233 | 115.2962 | 4194.1567 | 18370.4062
[7 empty] | Industrial | #6, Normal Firing | 4166.6667 | 18250 | 4.1667 | 18.25 | 26.3233 | 115.2962 | 4197.1567 | 18383.5462
[7 empty] | Industrial | #5, Normal Firing | 4166.6667 | 18250 | 4.1667 | 18.25 | 26.3233 | 115.2962 | 4197.1567 | 18383.5462
[7 empty] | Industrial | #2 Distillate, Normal | 3982.1429 | 17441.7857 | 0.23214 | 1.0168 | 13.8357 | 60.6004 | 3996.2107 | 17503.4029 | Match
[7 empty] | Industrial | #1 Distillate, Normal | 3839.2857 | 16816.0714 | 0.23214 | 1.0168 | 13.8357 | 60.6004 | 3853.3536 | 16877.6886
[7 empty] | Industrial | #4, Normal Firing | 4166.6667 | 18250 | 0.21667 | 0.949 | 26.3233 | 115.2962 | 4193.2067 | 18366.2452
[7 empty] | Comercial | #6, Normal Firing | 4166.6667 | 18250 | 1.9792 | 8.6687 | 26.3233 | 115.2962 | 4194.9692 | 18373.9649
[7 empty] | Comercial | #5, Normal Firing | 4166.6667 | 18250 | 1.9792 | 8.6687 | 26.3233 | 115.2962 | 4194.9692 | 18373.9649
[7 empty] | Comercial | #2 Distillate, Normal | 3982.1429 | 17441.7857 | 0.96429 | 4.2236 | 13.8357 | 60.6004 | 3996.9429 | 17506.6097
[7 empty] | Comercial | #1 Distillate, Normal | 3839.2857 | 16816.0714 | 0.96429 | 4.2236 | 13.8357 | 60.6004 | 3854.0857 | 16880.8954
[7 empty] | Comercial | #4, Normal Firing | 4166.6667 | 18250 | 0.9 | 3.942 | 26.3233 | 115.2962 | 4193.89 | 18369.2382
[7 empty] | Residential | Residential Furnace #2 | 3982.1429 | 17441.7857 | 7.9464 | 34.8054 | 2.6607 | 11.6539 | 3992.75 | 17488.245
[7 empty] | Residential | Residential Furnace #1 | 3839.2857 | 16816.0714 | 7.9464 | 34.8054 | 2.6607 | 11.6539 | 3849.8929 | 16862.5307
[6 empty] | POM |  | Table 1.3-8 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[8 empty] | #6, Normal Firing | 0.0013 | 8.6667e-06 | 0.00021667 | 0.000949
[8 empty] | Distillate, Normal | 0.0033 | 2.3571e-05 | 0.00058929 | 0.0025811 | Match
[6 empty] | Formaldehyde |  | Table 1.3-8 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[8 empty] | #6, Normal Firing | 0.061 | 0.00040667 | 0.010167 | 0.04453
[8 empty] | Distillate, Normal | 0.061 | 0.00043571 | 0.010893 | 0.047711 | Match
[10 empty] | Residual Oil |  |  |  | Distillate Oil
[6 empty] | HAP - Organic |  | Table 1.3-9 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check | lb/MMBtu | lb/hr | Ton/year | Check
[8 empty] | Benzene | 0.000214 | 1.4267e-06 | 3.5667e-05 | 0.00015622 |  | 1.5286e-06 | 3.8214e-05 | 0.00016738 | Match
[8 empty] | Ethylbenzene | 6.36e-05 | 4.24e-07 | 1.06e-05 | 4.6428e-05 |  | 4.5429e-07 | 1.1357e-05 | 4.9744e-05 | Match
[8 empty] | Naphthalene | 0.00113 | 7.5333e-06 | 0.00018833 | 0.0008249 |  | 8.0714e-06 | 0.00020179 | 0.00088382 | Match
[8 empty] | 1,1,1-Trichloroethane | 0.000236 | 1.5733e-06 | 3.9333e-05 | 0.00017228 |  | 1.6857e-06 | 4.2143e-05 | 0.00018459 | Match
[8 empty] | Toluene | 0.0062 | 4.1333e-05 | 0.0010333 | 0.004526 |  | 4.4286e-05 | 0.0011071 | 0.0048493 | Match
[8 empty] | o-Xylene | 0.000109 | 7.2667e-07 | 1.8167e-05 | 7.957e-05 |  | 7.7857e-07 | 1.9464e-05 | 8.5254e-05 | Match
[8 empty] | Acenaphthene | 2.11e-05 | 1.4067e-07 | 3.5167e-06 | 1.5403e-05 |  | 1.5071e-07 | 3.7679e-06 | 1.6503e-05 | Match
[8 empty] | Acenaphthylene | 2.53e-07 | 1.6867e-09 | 4.2167e-08 | 1.8469e-07 |  | 1.8071e-09 | 4.5179e-08 | 1.9788e-07 | Match
[8 empty] | Anthracene | 1.22e-06 | 8.1333e-09 | 2.0333e-07 | 8.906e-07 |  | 8.7143e-09 | 2.1786e-07 | 9.5421e-07 | Match
[8 empty] | Benz(a)anthracene | 4.01e-06 | 2.6733e-08 | 6.6833e-07 | 2.9273e-06 |  | 2.8643e-08 | 7.1607e-07 | 3.1364e-06 | Match
[8 empty] | Benzo(b,k)fluoranthene | 1.48e-06 | 9.8667e-09 | 2.4667e-07 | 1.0804e-06 |  | 1.0571e-08 | 2.6429e-07 | 1.1576e-06 | Match
[8 empty] | Benzo(g,h,i)perylene | 2.26e-06 | 1.5067e-08 | 3.7667e-07 | 1.6498e-06 |  | 1.6143e-08 | 4.0357e-07 | 1.7676e-06 | Match
[8 empty] | Chrysene | 2.38e-06 | 1.5867e-08 | 3.9667e-07 | 1.7374e-06 |  | 1.7e-08 | 4.25e-07 | 1.8615e-06 | Match
[8 empty] | Dibenzo(a,h)anthracene | 1.67e-06 | 1.1133e-08 | 2.7833e-07 | 1.2191e-06 |  | 1.1929e-08 | 2.9821e-07 | 1.3062e-06 | Match
[8 empty] | Fluoranthene | 4.84e-06 | 3.2267e-08 | 8.0667e-07 | 3.5332e-06 |  | 3.4571e-08 | 8.6429e-07 | 3.7856e-06 | Match
[8 empty] | Fluorene | 4.47e-06 | 2.98e-08 | 7.45e-07 | 3.2631e-06 |  | 3.1929e-08 | 7.9821e-07 | 3.4962e-06 | Match
[8 empty] | Indeno(1,2,3-cd)pyrene | 2.14e-06 | 1.4267e-08 | 3.5667e-07 | 1.5622e-06 |  | 1.5286e-08 | 3.8214e-07 | 1.6738e-06 | Match
[8 empty] | Phenanathrene | 1.05e-05 | 7e-08 | 1.75e-06 | 7.665e-06 |  | 7.5e-08 | 1.875e-06 | 8.2125e-06 | Match
[8 empty] | Pyrene | 4.25e-06 | 2.8333e-08 | 7.0833e-07 | 3.1025e-06 |  | 3.0357e-08 | 7.5893e-07 | 3.3241e-06 | Match
[8 empty] | OCDD | 3.1e-09 | 2.0667e-11 | 5.1667e-10 | 2.263e-09 |  | 2.2143e-11 | 5.5357e-10 | 2.4246e-09 | Match
Distillate Oil
[6 empty] | HAP - Metal |  | Table 1.3-10 | lb/10^12 Btu | lb/10^3 gal |  |  |  | lb/MMBtu | lb/hr | Ton/year | Check
[8 empty] | Arsenic | 4 | 0.00056 |  |  |  | 4e-06 | 0.0001 | 0.000438 | Match
[8 empty] | Beryllium | 3 | 0.00042 |  |  |  | 3e-06 | 7.5e-05 | 0.0003285 | Match
[8 empty] | Cadmium | 3 | 0.00042 |  |  |  | 3e-06 | 7.5e-05 | 0.0003285 | Match
[8 empty] | Chromium | 3 | 0.00042 |  |  |  | 3e-06 | 7.5e-05 | 0.0003285 | Match
[8 empty] | Lead | 9 | 0.00126 |  |  |  | 9e-06 | 0.000225 | 0.0009855 | Match
[8 empty] | Mercury | 3 | 0.00042 |  |  |  | 3e-06 | 7.5e-05 | 0.0003285 | Match
[8 empty] | Manganese | 6 | 0.00084 |  |  |  | 6e-06 | 0.00015 | 0.000657 | Match
[8 empty] | Nickel | 3 | 0.00042 |  |  |  | 3e-06 | 7.5e-05 | 0.0003285 | Match
[8 empty] | Selenium | 15 | 0.0021 |  |  |  | 1.5e-05 | 0.000375 | 0.0016425 | Match
Residual Oil
[6 empty] | HAP - Metal |  | Table 1.3-11 | lb/10^3 gal | lb/MMBtu | lb/hr | Ton/year | Check
[8 empty] | Antimony | 0.00525 | 3.5e-05 | 0.000875 | 0.0038325
[8 empty] | Arsenic | 0.00132 | 8.8e-06 | 0.00022 | 0.0009636
[8 empty] | Beryllium | 2.78e-05 | 1.8533e-07 | 4.6333e-06 | 2.0294e-05
[8 empty] | Cadmium | 0.000398 | 2.6533e-06 | 6.6333e-05 | 0.00029054
[8 empty] | Chromium | 0.000845 | 5.6333e-06 | 0.00014083 | 0.00061685
[8 empty] | Chromium VI | 0.000248 | 1.6533e-06 | 4.1333e-05 | 0.00018104
[8 empty] | Cobalt | 0.00602 | 4.0133e-05 | 0.0010033 | 0.0043946
[8 empty] | Lead | 0.00151 | 1.0067e-05 | 0.00025167 | 0.0011023
[8 empty] | Manganese | 0.003 | 2e-05 | 0.0005 | 0.00219
[8 empty] | Mercury | 0.000113 | 7.5333e-07 | 1.8833e-05 | 8.249e-05
[8 empty] | Nickel | 0.0845 | 0.00056333 | 0.014083 | 0.061685
[8 empty] | Selenium | 0.000683 | 4.5533e-06 | 0.00011383 | 0.00049859
[6 empty] | Total HAP |  | Total HAP |  |  | lb/hr | Ton/year | Check |  | lb/hr | Ton/year | Check
[11 empty] | 0.029038 | 0.12719 |  |  | 0.014138 | 0.061925 | Match