## Engine NG
Natural Gas-Fired Engines | [6 empty] | 7000 | BTU/hp-hr
Equipment Details
Rating | 750 | hp = (559.8 kw) | Emergency Engines should equal 100 hours of operation per year
Operational Hours | 8760 | hours/year
Engine Type | 4-Stroke Lean-Burn | [5 empty] | 2-Stroke Lean-Burn |  |  |  |  | 4-Stroke Lean-Burn |  |  |  |  | 4-Stroke Rich-Burn
[7 empty] | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check
Criteria Pollutant | Emission Standards (g/hp-hr) | Emission Factor (lb/MMBtu) | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | NOX @ 90-105% Load | 3.17 | 0.02219 | 16.6425 | 72.8942 |  | 4.08 | 0.02856 | 21.42 | 93.8196 | Match | 2.21 | 0.01547 | 11.6025 | 50.8189
NOX |  | 4.08 | 21.42 | 93.8196 | Manufacturer Data, AP-42 Table 3.2-1, Table 3.2-2, & Table 3.2-3 | NOX @ <90% Load | 1.94 | 0.01358 | 10.185 | 44.6103 |  | 0.847 | 0.005929 | 4.4467 | 19.4768 |  | 2.27 | 0.01589 | 11.9175 | 52.1987
CO |  | 0.317 | 1.6643 | 7.2894 |  | CO @ 90-105% Load | 0.386 | 0.002702 | 2.0265 | 8.8761 |  | 0.317 | 0.002219 | 1.6643 | 7.2894 | Match | 3.72 | 0.02604 | 19.53 | 85.5414
PM10 |  | 0.0099871 | 0.052432 | 0.22965 |  | CO @ <90% Load | 0.353 | 0.002471 | 1.8533 | 8.1172 |  | 0.557 | 0.003899 | 2.9243 | 12.8082 |  | 3.51 | 0.02457 | 18.4275 | 80.7125
PM2.5 |  | 0.0099871 | 0.052432 | 0.22965 |  | CO2 | 110 | 0.77 | 577.5 | 2529.45 | Match | 110 | 0.77 | 577.5 | 2529.45 | Match | 110 | 0.77 | 577.5 | 2529.45 | Match
VOC |  | 0.118 | 0.6195 | 2.7134 |  | SO2 | 0.000588 | 4.116e-06 | 0.003087 | 0.013521 | Match | 0.000588 | 4.116e-06 | 0.003087 | 0.013521 | Match | 0.000588 | 4.116e-06 | 0.003087 | 0.013521 | Match
SO2 |  | 0.000588 | 0.003087 | 0.013521 |  | TOC | 1.64 | 0.01148 | 8.61 | 37.7118 |  | 1.47 | 0.01029 | 7.7175 | 33.8026 |  | 0.358 | 0.002506 | 1.8795 | 8.2322
HAP |  |  | 0.37903 | 1.6601 | See Below | Methane | 1.45 | 0.01015 | 7.6125 | 33.3428 |  | 1.25 | 0.00875 | 6.5625 | 28.7438 | Match | 0.23 | 0.00161 | 1.2075 | 5.2889
[6 empty] | VOC | 0.12 | 0.00084 | 0.63 | 2.7594 |  | 0.118 | 0.000826 | 0.6195 | 2.7134 | Match | 0.0296 | 0.0002072 | 0.1554 | 0.68065
Green House Gas Pollutant | Global Warming Potential | Emission Factor (lb/MMBtu) | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | PM10 - filterable | 0.0384 | 0.0002688 | 0.2016 | 0.88301 |  | 7.71e-05 | 5.397e-07 | 0.00040478 | 0.0017729 |  | 0.0095 | 6.65e-05 | 0.049875 | 0.21845
CO2 (mass basis) | 1 | 110 | 577.5 | 2529.45 | AP-42 Table 3.2-1, Table 3.2-2, & Table 3.2-3 | PM2.5 - filterable | 0.0384 | 0.0002688 | 0.2016 | 0.88301 |  | 7.71e-05 | 5.397e-07 | 0.00040478 | 0.0017729 |  | 0.0095 | 6.65e-05 | 0.049875 | 0.21845
Methane (mass basis) | 25 | 1.25 | 6.5625 | 28.7437 |  | PM - Condensable | 0.00991 | 6.937e-05 | 0.052028 | 0.22788 |  | 0.00991 | 6.937e-05 | 0.052028 | 0.22788 |  | 0.00991 | 6.937e-05 | 0.052028 | 0.22788
CO2e |  |  |  | 3248.0437 |  | PM10 - Total | 0.04831 |  | 0.25363 | 1.1109 |  | 0.0099871 |  | 0.052432 | 0.22965 | Match | 0.01941 |  | 0.1019 | 0.44633
[6 empty] | PM2.5 - Total | 0.04831 |  | 0.25363 | 1.1109 |  | 0.0099871 |  | 0.052432 | 0.22965 | Match | 0.01941 |  | 0.1019 | 0.44633
Hazardous Air Pollutant | Emission Factor (lb/MMBtu) |  | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | HAP | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check | lb/MMBtu | lb/hp-hr | lb/hr | Ton/year | Check
1,1,2,2-Tetrachloroethane |  | 4e-05 | 0.00021 | 0.0009198 | AP-42 Table 3.2-1, Table 3.2-2, & Table 3.2-3 (Some HAP do not popluate based on the type of engine selected. AP-42 does not list certain HAP for certain types of engines.) | 1,1,2,2-Tetrachloroethane | 6.63e-05 | 4.641e-07 | 0.00034808 | 0.0015246 |  | 4e-05 | 2.8e-07 | 0.00021 | 0.0009198 | Match | 2.53e-05 | 1.771e-07 | 0.00013282 | 0.00058177
1,1,2-Trichloroethane |  | 3.18e-05 | 0.00016695 | 0.00073124 |  | 1,1,2-Trichloroethane | 5.27e-05 | 3.689e-07 | 0.00027668 | 0.0012118 |  | 3.18e-05 | 2.226e-07 | 0.00016695 | 0.00073124 | Match | 1.53e-05 | 1.071e-07 | 8.0325e-05 | 0.00035182
1,3-Butadiene |  | 0.000267 | 0.0014017 | 0.0061397 |  | 1,3-Butadiene | 0.00082 | 5.74e-06 | 0.004305 | 0.018856 |  | 0.000267 | 1.869e-06 | 0.0014018 | 0.0061397 | Match | 0.000663 | 4.641e-06 | 0.0034807 | 0.015246
1,3-Dichloropropene |  | 2.64e-05 | 0.0001386 | 0.00060707 |  | 1,3-Dichloropropene | 4.38e-05 | 3.066e-07 | 0.00022995 | 0.0010072 |  | 2.64e-05 | 1.848e-07 | 0.0001386 | 0.00060707 | Match | 1.27e-05 | 8.89e-08 | 6.6675e-05 | 0.00029204
2,2,4-Trimethylpentane |  | 0.00025 | 0.0013125 | 0.0057488 |  | 2,2,4-Trimethylpentane | 0.000846 | 5.922e-06 | 0.0044415 | 0.019454 |  | 0.00025 | 1.75e-06 | 0.0013125 | 0.0057488 | Match
2-Methylnaphthalene |  | 3.32e-05 | 0.0001743 | 0.00076343 |  | 2-Methylnaphthalene | 2.14e-05 | 1.498e-07 | 0.00011235 | 0.00049209 |  | 3.32e-05 | 2.324e-07 | 0.0001743 | 0.00076343 | Match
Acenaphthene |  | 1.25e-06 | 6.5625e-06 | 2.8744e-05 |  | Acenaphthene | 1.33e-06 | 9.31e-09 | 6.9825e-06 | 3.0583e-05 |  | 1.25e-06 | 8.75e-09 | 6.5625e-06 | 2.8744e-05 | Match
Acenaphthylene |  | 5.53e-06 | 2.9033e-05 | 0.00012716 |  | Acenaphthylene | 3.17e-06 | 2.219e-08 | 1.6643e-05 | 7.2894e-05 |  | 5.53e-06 | 3.871e-08 | 2.9033e-05 | 0.00012716 | Match
Acetaldehyde |  | 0.00836 | 0.04389 | 0.19224 |  | Acetaldehyde | 0.00776 | 5.432e-05 | 0.04074 | 0.17844 |  | 0.00836 | 5.852e-05 | 0.04389 | 0.19224 | Match | 0.00279 | 1.953e-05 | 0.014648 | 0.064156
Acrolein |  | 0.00514 | 0.026985 | 0.11819 |  | Acrolein | 0.00778 | 5.446e-05 | 0.040845 | 0.1789 |  | 0.00514 | 3.598e-05 | 0.026985 | 0.11819 | Match | 0.00263 | 1.841e-05 | 0.013808 | 0.060477
[6 empty] | Anthracene | 7.18e-07 | 5.026e-09 | 3.7695e-06 | 1.651e-05 | [5 empty] | Match |  |  |  |  | Match
[6 empty] | Benz(a)anthracene | 3.36e-07 | 2.352e-09 | 1.764e-06 | 7.7263e-06 | [5 empty] | Match |  |  |  |  | Match
Benzene |  | 0.00044 | 0.00231 | 0.010118 |  | Benzene | 0.00194 | 1.358e-05 | 0.010185 | 0.04461 |  | 0.00044 | 3.08e-06 | 0.00231 | 0.010118 | Match | 0.00158 | 1.106e-05 | 0.008295 | 0.036332
[6 empty] | Benzo(a)pyrene | 5.68e-09 | 3.976e-11 | 2.982e-08 | 1.3061e-07 | [5 empty] | Match |  |  |  |  | Match
Benzo(b)fluoranthene |  | 1.66e-07 | 8.715e-07 | 3.8172e-06 |  | Benzo(b)fluoranthene | 8.51e-09 | 5.957e-11 | 4.4677e-08 | 1.9569e-07 |  | 1.66e-07 | 1.162e-09 | 8.715e-07 | 3.8172e-06 | Match
Benzo(e)pyrene |  | 4.15e-07 | 2.1788e-06 | 9.5429e-06 |  | Benzo(e)pyrene | 2.34e-08 | 1.638e-10 | 1.2285e-07 | 5.3808e-07 |  | 4.15e-07 | 2.905e-09 | 2.1788e-06 | 9.5429e-06 | Match
benzo(g,h,i)perylene |  | 4.14e-07 | 2.1735e-06 | 9.5199e-06 |  | benzo(g,h,i)perylene | 2.48e-08 | 1.736e-10 | 1.302e-07 | 5.7028e-07 |  | 4.14e-07 | 2.898e-09 | 2.1735e-06 | 9.5199e-06 | Match
[6 empty] | Benzo(k)fluoranthene | 4.26e-09 | 2.982e-11 | 2.2365e-08 | 9.7959e-08 | [5 empty] | Match |  |  |  |  | Match
Biphenyl |  | 0.000212 | 0.001113 | 0.0048749 |  | Biphenyl | 3.95e-06 | 2.765e-08 | 2.0737e-05 | 9.083e-05 |  | 0.000212 | 1.484e-06 | 0.001113 | 0.0048749 | Match
Carbon Tetrachloride |  | 3.67e-05 | 0.00019267 | 0.00084392 |  | Carbon Tetrachloride | 6.07e-05 | 4.249e-07 | 0.00031867 | 0.0013958 |  | 3.67e-05 | 2.569e-07 | 0.00019267 | 0.00084392 | Match | 1.77e-05 | 1.239e-07 | 9.2925e-05 | 0.00040701
Chlorobenzene |  | 3.04e-05 | 0.0001596 | 0.00069905 |  | Chlorobenzene | 4.44e-05 | 3.108e-07 | 0.0002331 | 0.001021 |  | 3.04e-05 | 2.128e-07 | 0.0001596 | 0.00069905 | Match | 1.29e-05 | 9.03e-08 | 6.7725e-05 | 0.00029664
Chloroform |  | 2.85e-05 | 0.00014962 | 0.00065536 |  | Chloroform | 4.71e-05 | 3.297e-07 | 0.00024727 | 0.0010831 |  | 2.85e-05 | 1.995e-07 | 0.00014962 | 0.00065536 | Match | 1.37e-05 | 9.59e-08 | 7.1925e-05 | 0.00031503
Chrysene |  | 6.93e-07 | 3.6383e-06 | 1.5936e-05 |  | Chrysene | 6.72e-07 | 4.704e-09 | 3.528e-06 | 1.5453e-05 |  | 6.93e-07 | 4.851e-09 | 3.6382e-06 | 1.5936e-05 | Match
Ethylbenzene |  | 3.97e-05 | 0.00020843 | 0.0009129 |  | Ethylbenzene | 0.000108 | 7.56e-07 | 0.000567 | 0.0024835 |  | 3.97e-05 | 2.779e-07 | 0.00020843 | 0.0009129 | Match | 2.48e-05 | 1.736e-07 | 0.0001302 | 0.00057028
Ethylene Dibromide |  | 4.43e-05 | 0.00023258 | 0.0010187 |  | Ethylene Dibromide | 7.34e-05 | 5.138e-07 | 0.00038535 | 0.0016878 |  | 4.43e-05 | 3.101e-07 | 0.00023258 | 0.0010187 | Match | 2.13e-05 | 1.491e-07 | 0.00011182 | 0.00048979
Fluoranthene |  | 1.11e-06 | 5.8275e-06 | 2.5524e-05 |  | Fluoranthene | 3.61e-07 | 2.527e-09 | 1.8952e-06 | 8.3012e-06 |  | 1.11e-06 | 7.77e-09 | 5.8275e-06 | 2.5524e-05 | Match
Fluorene |  | 5.67e-06 | 2.9768e-05 | 0.00013038 |  | Fluorene | 1.69e-06 | 1.183e-08 | 8.8725e-06 | 3.8862e-05 |  | 5.67e-06 | 3.969e-08 | 2.9767e-05 | 0.00013038 | Match
Formaldehyde |  | 0.0528 | 0.2772 | 1.2141 |  | Formaldehyde | 0.0552 | 0.0003864 | 0.2898 | 1.2693 |  | 0.0528 | 0.0003696 | 0.2772 | 1.2141 | Match | 0.0205 | 0.0001435 | 0.10762 | 0.4714
[6 empty] | Indeno(1,2,3-c,d)pyrene | 9.93e-09 | 6.951e-11 | 5.2133e-08 | 2.2834e-07 | [5 empty] | Match |  |  |  |  | Match
Methanol |  | 0.0025 | 0.013125 | 0.057487 |  | Methanol | 0.00248 | 1.736e-05 | 0.01302 | 0.057028 |  | 0.0025 | 1.75e-05 | 0.013125 | 0.057487 | Match | 0.00306 | 2.142e-05 | 0.016065 | 0.070365
Methylene Chloride |  | 2e-05 | 0.000105 | 0.0004599 |  | Methylene Chloride | 0.000147 | 1.029e-06 | 0.00077175 | 0.0033803 |  | 2e-05 | 1.4e-07 | 0.000105 | 0.0004599 | Match | 4.12e-05 | 2.884e-07 | 0.0002163 | 0.00094739
n-Hexane |  | 0.00111 | 0.0058275 | 0.025524 |  | n-Hexane | 0.000445 | 3.115e-06 | 0.0023362 | 0.010233 |  | 0.00111 | 7.77e-06 | 0.0058275 | 0.025524 | Match
Naphthalene |  | 7.44e-05 | 0.0003906 | 0.0017108 |  | Naphthalene | 9.63e-05 | 6.741e-07 | 0.00050557 | 0.0022144 |  | 7.44e-05 | 5.208e-07 | 0.0003906 | 0.0017108 | Match | 9.71e-05 | 6.797e-07 | 0.00050977 | 0.0022328
PAH |  | 2.69e-05 | 0.00014123 | 0.00061857 |  | PAH | 0.000134 | 9.38e-07 | 0.0007035 | 0.0030813 |  | 2.69e-05 | 1.883e-07 | 0.00014122 | 0.00061857 | Match | 0.000141 | 9.87e-07 | 0.00074025 | 0.0032423
[6 empty] | Perylene | 4.97e-09 | 3.479e-11 | 2.6092e-08 | 1.1429e-07 | [5 empty] | Match |  |  |  |  | Match
Phenanthrene |  | 1.04e-05 | 5.46e-05 | 0.00023915 |  | Phenanthrene | 3.53e-06 | 2.471e-08 | 1.8532e-05 | 8.1172e-05 |  | 1.04e-05 | 7.28e-08 | 5.46e-05 | 0.00023915 | Match
Phenol |  | 2.4e-05 | 0.000126 | 0.00055188 |  | Phenol | 4.21e-05 | 2.947e-07 | 0.00022103 | 0.00096809 |  | 2.4e-05 | 1.68e-07 | 0.000126 | 0.00055188 | Match
Pyrene |  | 1.36e-06 | 7.14e-06 | 3.1273e-05 |  | Pyrene | 5.84e-07 | 4.088e-09 | 3.066e-06 | 1.3429e-05 |  | 1.36e-06 | 9.52e-09 | 7.14e-06 | 3.1273e-05 | Match
Styrene |  | 2.36e-05 | 0.0001239 | 0.00054268 |  | Styrene | 5.48e-05 | 3.836e-07 | 0.0002877 | 0.0012601 |  | 2.36e-05 | 1.652e-07 | 0.0001239 | 0.00054268 | Match | 1.19e-05 | 8.33e-08 | 6.2475e-05 | 0.00027364
Tetrachloroethane |  | 2.48e-06 | 1.302e-05 | 5.7028e-05 |  | Tetrachloroethane | [5 empty] | 2.48e-06 | 1.736e-08 | 1.302e-05 | 5.7028e-05 | Match
Toluene |  | 0.000408 | 0.002142 | 0.009382 |  | Toluene | 0.000963 | 6.741e-06 | 0.0050557 | 0.022144 |  | 0.000408 | 2.856e-06 | 0.002142 | 0.009382 | Match | 0.000558 | 3.906e-06 | 0.0029295 | 0.012831
Vinyl Chloride |  | 1.49e-05 | 7.8225e-05 | 0.00034263 |  | Vinyl Chloride | 2.47e-05 | 1.729e-07 | 0.00012967 | 0.00056798 |  | 1.49e-05 | 1.043e-07 | 7.8225e-05 | 0.00034263 | Match | 7.18e-06 | 5.026e-08 | 3.7695e-05 | 0.0001651
Xylene |  | 0.000184 | 0.000966 | 0.0042311 |  | Xylene | 0.000268 | 1.876e-06 | 0.001407 | 0.0061627 |  | 0.000184 | 1.288e-06 | 0.000966 | 0.0042311 | Match | 0.000195 | 1.365e-06 | 0.0010238 | 0.004484
[6 empty] | Total HAP |  |  | 0.41756 | 1.8289 |  |  |  | 0.37903 | 1.6601 | Match |  |  | 0.17019 | 0.74545