## Engine Diesel
Diesel-Fired Engines | [6 empty] | 7000 | BTU/hp-hr
Equipment Details
Rating | 700 | hp = (522.4 kw) | Emergency Engines should equal 100 hours of operation per year |  |  |  | Table 3.3-1 |  |  |  |  | Table 3.4-1
Operational Hours | 8760 | hours/year |  |  |  |  | <600 hp |  |  |  |  | >600 hp
Sulfur Content | 15 | ppm or 0.0015% |  |  |  |  | lb/hp-hr | lb/hr | Ton/year | Check |  | EF x S | lb/hp-hr | lb/hr | Ton/year | Check
[6 empty] | Nox - Uncontrolled | 0.031 | 21.7 | 95.046 |  |  |  | 0.024 | 16.8 | 73.584 | Match
Criteria Pollutant | Emission Standards (g/hp-hr) | Emission Factor (lb/hp-hr) | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | Nox - Controlled | [6 empty] | 0.013 | 9.1 | 39.858
NOX |  | 0.024 | 16.8 | 73.584 | Manufacturer Data, AP-42 Table 3.3-1, & Table 3.4-1 | CO | 0.00668 | 4.676 | 20.4809 |  |  |  | 0.0055 | 3.85 | 16.863 | Match
CO |  | 0.0055 | 3.85 | 16.863 |  | SO2 | 0.00205 | 1.435 | 6.2853 |  |  | 0.00809 | 1.2135e-05 | 0.0084945 | 0.037206 | Match | Used>600 hp to allow for sulfur content of fuel
PM10 |  | 0.0007 | 0.49 | 2.1462 |  | PM10 | 0.0022 | 1.54 | 6.7452 |  |  |  | 0.0007 | 0.49 | 2.1462 | Match | Table 3.3-1 does not allow for a sulfur content.
PM2.5 |  | 0.0007 | 0.49 | 2.1462 |  | CO2 | 1.15 | 805 | 3525.9 |  |  |  | 1.16 | 812 | 3556.56 | Match | To be more representatvie, Table 3.4-1 was used for all engine sizes.
VOC |  | 0.00064155 | 0.44909 | 1.967 |  | Aldehydes | 0.000463 | Not used, included in HAP below.
SO2 |  | 1.2135e-05 | 0.0084945 | 0.037206 | AP-42 Table 3.4-1 | TOC | 0.00251 | 1.757 | 7.6957 |  |  |  | 0.000705 | 0.4935 | 2.1615 |  | for engines >600 hp, TOC is 91% VOC & 9% methane
HAP |  |  | 0.0077102 | 0.033771 | See Below | VOC | 0.0025141 | 1.7599 | 7.7082 |  |  | 91% | 0.00064155 | 0.44909 | 1.967 | Match
[6 empty] | Methane | [5 empty] | 9% | 6.345e-05 | 0.044415 | 0.19454 | Match
Green House Gas Pollutant | Global Warming Potential | Emission Factor (lb/hp-hr) | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | Exhaust | 0.00247
CO2 (mass basis) | 1 | 1.16 | 812 | 3556.56 | AP-42 Table 3.3-1 & Table 3.4-1 | Evaporative | 0
Methane (mass basis) | 25 | 6.345e-05 | 0.044415 | 0.19454 |  | Crankcase | 4.41e-05
CO2e |  |  |  | 3561.4234 |  | Refueling | 0
Hazardous Air Pollutant | Emission Factor (lb/MMBtu) |  | Emission Rate (lbs/hr) | Emission Total (tons/year) | Reference | HAP | Table 3.3-2 <600 hp (lb/MMBtu) | lb/hp-hr | lb/hr | Ton/year | Check | Table 3.4-3 >600 hp (lb/MMBtu) | lb/hp-hr | lb/hr | Ton/year | Check
Benzene |  | 0.000776 | 0.0038024 | 0.016655 | AP-42 Table 3.3-2, Table 3.4-3, & Table 3.4-4 (1,3-Butadiene will not popluate if the engine size is greater than 600 hp. AP-42 does not list 1,3-Butadiene for engines greater than 600 hp.) | Benzene | 0.000933 | 6.531e-06 | 0.0045717 | 0.020024 |  | 0.000776 | 5.432e-06 | 0.0038024 | 0.016655 | Match
Toluene |  | 0.000281 | 0.0013769 | 0.0060308 |  | Toluene | 0.000409 | 2.863e-06 | 0.0020041 | 0.008778 |  | 0.000281 | 1.967e-06 | 0.0013769 | 0.0060308 | Match
Xylenes |  | 0.000193 | 0.0009457 | 0.0041422 |  | Xylenes | 0.000285 | 1.995e-06 | 0.0013965 | 0.0061167 |  | 0.000193 | 1.351e-06 | 0.0009457 | 0.0041422 | Match
[6 empty] | 1,3-Butadiene | 3.91e-05 | 2.737e-07 | 0.00019159 | 0.00083916 | [5 empty] | Match
Formaldehyde |  | 7.89e-05 | 0.00038661 | 0.0016934 |  | Formaldehyde | 0.00118 | 8.26e-06 | 0.005782 | 0.025325 |  | 7.89e-05 | 5.523e-07 | 0.00038661 | 0.0016934 | Match
Acetaldehyde |  | 2.52e-05 | 0.00012348 | 0.00054084 |  | Acetaldehyde | 0.000767 | 5.369e-06 | 0.0037583 | 0.016461 |  | 2.52e-05 | 1.764e-07 | 0.00012348 | 0.00054084 | Match
Acrolein |  | 7.88e-06 | 3.8612e-05 | 0.00016912 |  | Acrolein | 9.25e-05 | 6.475e-07 | 0.00045325 | 0.0019852 |  | 7.88e-06 | 5.516e-08 | 3.8612e-05 | 0.00016912 | Match
Naphthalene |  | 0.00013 | 0.000637 | 0.0027901 |  | Naphthalene | 8.48e-05 | 5.936e-07 | 0.00041552 | 0.00182 |  | 0.00013 | 9.1e-07 | 0.000637 | 0.0027901 | Match
Acenaphthylene |  | 9.23e-06 | 4.5227e-05 | 0.00019809 |  | Acenaphthylene | 5.06e-06 | 3.542e-08 | 2.4794e-05 | 0.0001086 |  | 9.23e-06 | 6.461e-08 | 4.5227e-05 | 0.00019809 | Match
Acenaphthene |  | 4.68e-06 | 2.2932e-05 | 0.00010044 |  | Acenaphthene | 1.42e-06 | 9.94e-09 | 6.958e-06 | 3.0476e-05 |  | 4.68e-06 | 3.276e-08 | 2.2932e-05 | 0.00010044 | Match
Fluorene |  | 1.28e-05 | 6.272e-05 | 0.00027471 |  | Fluorene | 2.92e-05 | 2.044e-07 | 0.00014308 | 0.00062669 |  | 1.28e-05 | 8.96e-08 | 6.272e-05 | 0.00027471 | Match
Phenanthrene |  | 4.08e-05 | 0.00019992 | 0.00087565 |  | Phenanthrene | 2.94e-05 | 2.058e-07 | 0.00014406 | 0.00063098 |  | 4.08e-05 | 2.856e-07 | 0.00019992 | 0.00087565 | Match
Anthracene |  | 1.23e-06 | 6.027e-06 | 2.6398e-05 |  | Anthracene | 1.87e-06 | 1.309e-08 | 9.163e-06 | 4.0134e-05 |  | 1.23e-06 | 8.61e-09 | 6.027e-06 | 2.6398e-05 | Match
Fluoranthene |  | 4.03e-06 | 1.9747e-05 | 8.6492e-05 |  | Fluoranthene | 7.61e-06 | 5.327e-08 | 3.7289e-05 | 0.00016333 |  | 4.03e-06 | 2.821e-08 | 1.9747e-05 | 8.6492e-05 | Match
Pyrene |  | 3.71e-06 | 1.8179e-05 | 7.9624e-05 |  | Pyrene | 4.78e-06 | 3.346e-08 | 2.3422e-05 | 0.00010259 |  | 3.71e-06 | 2.597e-08 | 1.8179e-05 | 7.9624e-05 | Match
Benz(a)anthracene |  | 6.22e-07 | 3.0478e-06 | 1.3349e-05 |  | Benz(a)anthracene | 1.68e-06 | 1.176e-08 | 8.232e-06 | 3.6056e-05 |  | 6.22e-07 | 4.354e-09 | 3.0478e-06 | 1.3349e-05 | Match
Chrysene |  | 1.53e-06 | 7.497e-06 | 3.2837e-05 |  | Chrysene | 3.53e-07 | 2.471e-09 | 1.7297e-06 | 7.5761e-06 |  | 1.53e-06 | 1.071e-08 | 7.497e-06 | 3.2837e-05 | Match
Benzo(b)fluoranthene |  | 1.11e-06 | 5.439e-06 | 2.3823e-05 |  | Benzo(b)fluoranthene | 9.91e-08 | 6.937e-10 | 4.8559e-07 | 2.1269e-06 |  | 1.11e-06 | 7.77e-09 | 5.439e-06 | 2.3823e-05 | Match
Benzo(k)fluoranthene |  | 2.18e-07 | 1.0682e-06 | 4.6787e-06 |  | Benzo(k)fluoranthene | 1.55e-07 | 1.085e-09 | 7.595e-07 | 3.3266e-06 |  | 2.18e-07 | 1.526e-09 | 1.0682e-06 | 4.6787e-06 | Match
Benzo(a)pyrene |  | 2.57e-07 | 1.2593e-06 | 5.5157e-06 |  | Benzo(a)pyrene | 1.88e-07 | 1.316e-09 | 9.212e-07 | 4.0349e-06 |  | 2.57e-07 | 1.799e-09 | 1.2593e-06 | 5.5157e-06 | Match
Indeno(1,2,3-cd)pyrene |  | 4.14e-07 | 2.0286e-06 | 8.8853e-06 |  | Indeno(1,2,3-cd)pyrene | 3.75e-07 | 2.625e-09 | 1.8375e-06 | 8.0483e-06 |  | 4.14e-07 | 2.898e-09 | 2.0286e-06 | 8.8853e-06 | Match
Dibenz(a,h)anthracene |  | 3.46e-07 | 1.6954e-06 | 7.4259e-06 |  | Dibenz(a,h)anthracene | 5.83e-07 | 4.081e-09 | 2.8567e-06 | 1.2512e-05 |  | 3.46e-07 | 2.422e-09 | 1.6954e-06 | 7.4259e-06 | Match
Benzo(g,h,l)perylene |  | 5.56e-07 | 2.7244e-06 | 1.1933e-05 |  | Benzo(g,h,l)perylene | 4.89e-07 | 3.423e-09 | 2.3961e-06 | 1.0495e-05 |  | 5.56e-07 | 3.892e-09 | 2.7244e-06 | 1.1933e-05 | Match