## Capacity Calculations
Division of Drinking Water — Water System Capacity Calculation Sheet (Last Update 3/30/2017)
*Enter the green cells only*
System Name |  | ABC Water System |  |  |  |  | System Number | 09999
1.1 Indoor Water Use
| Number of residential connections |  |  | - - - - - - - - - - - | - - - - - - - - - - | - - - - - - - - - | - - - - - - - - - | 200
| Number of other connections - - - |  |  | 2 |  |  | ERCs of other connections | 10 | (Example: water use of 2 factories equals to water use of 55 homes.)
[7 empty] | Total Equivalent Residential Connections (ERCs) | 210
MIN. REQUIREMENTS FOR INDOOR WATER USE
| Source |  | Storage
| gpd/ERC | Total (gpm) | Gallons/ERC | Total (gallons)
| 800 | 116.6667 | 400 | 84000
1.2 Outdoor Water Use
Is the drinking water used for outdoor irrigation?
| Residential ERCs using drinking water for irrigation |  |  |  |  | - - - - - - - - - | - - - > > > | 50
| Percentage of Residential ERCs using DW for irrigation |  |  |  |  | - - - - - - - - - | - - - > > > | 25% | Map Zones
| Average irrigated acreage per residential connection |  |  |  |  | - - - - - - - - - | - - - > > > | 0.05 | 1
| Total irrigated acreage of other connections (park, school, etc.) |  |  |  |  | - - - - - - - - - | - - - > > > | 10 | 2
(Enter notes here regarding whether and what % of irrigation water is supplied by PWS.) | [6 empty] | Irrigation zone | 3 | 3
4
5
| MIN. REQUIREMENTS FOR IRRIGATION USE | [7 empty] | 6
| Source |  | Storage
| gpd/ERC | Total (gpm) | Gallons/ERC | Total (gallons)
| 244.08 | 42.375 | 126.4 | 31600
1.3 Fire Flow Water Use
Does the water system provide fire protection?
| Maximum fire flow demand (in gpm) for water system or pressure zone | [6 empty] | 1000
| Maximum fire suppression duration (in hours) for water system or pressure zone | [6 empty] | 1
| Required Fire Suppression Storage (in gallons) |  |  |  | - - - - - - - - | - - - - - - - - - | - - - > > > | 60000
(*Verify req'd fire flow and duration with local fire code officials.* Enter notes here, e.g. fire official contact info or comments.)
2. Summary of Water System Capacity Requirements
MINIMUM REQUIREMENTS FOR WATER SYSTEM
| Source (indoor + outdoor) |  | Storage (indoor + outdoor + fire)
| gpd/ERC | Total (gpm) | Gallons/ERC | Total (gallons)
| 1044.08 | 159.0417 | 526.4 | 175600
2.1 Does this system have adequate source capacity (per R309-510-7)?
This source capacity assessment is a general overall system calculation. It may not reflect the variations in individual areas or pressure zones.
|  | Required Source Capacity | 159.0417 | gpm
|  | Existing Source Capacity | 180 | gpm
|  | Source Capacity Deficit | None | gpm
|  | Existing % of Total Req'd | 113.2%
2.2 Does this system have adequate storage capacity (per R309-510-8)?
This storage capacity assessment is a general overall system calculation. It may not reflect the variations in individual areas or pressure zones.
|  | Total Required Storage | 175600 | gal
|  | Existing Storage Capacity | 140000 | gal
|  | Storage Capacity Deficit | 35600 | gal
|  | Required Fire Storage | 60000 | gal
Is storage deficiency solely due to fire storage? |  |  | YES
|  | Existing % of Total Req'd | 79.73%
3. Transient PWS Indoor Water Use — ERC Calcuation (See R309-510, Tables 510-1, 2, & 4 for other facility types.)
MINIMUM REQUIREMENTS FOR INDOOR USE
|  |  |  | Source |  | Storage
Facility Type |  |  |  | GPD/person* | GPD/site or pad | Gallons/person | Gallon/site or pad | ERC/site or pad | Total # of sites/pads | ERCs
Modern Recreation Camp |  |  |  | 60 | 240 | 30 | 120 | 0.3 | 18 | 5.4
Semi-Developed Camp w/ flush toilets |  |  |  | 20 | 80 | 10 | 40 | 0.1 | 25 | 2.5
Semi-Developed Camp w/o flush toilets |  |  |  | 5 | 20 | 2.5 | 10 | 0.025 | 20 | 0.5
RV Park |  |  |  | N/A | 100 | N/A | 50 | 0.125 | 50 | 6.25
|  |  | Number of people per camp site | 4
|  |  |  | Source (GPD/vehicle) | Storage (Gal./vehicle) | ERC/1000 vehicles served | Vehicles served/day | ERCs
Roadway Rest Stop w/ flushometer valves |  |  |  | 7 | 3.5 | 8.75 | 700 | 6.125
4. Data Input for Calculating ERCs, Source and Storage | [5 empty] | 4.2 Summary - Existing Sources (enter in green cells below)
ABC Water System | [7 empty] | Total Existing Source Capacity (in gpm) | 180
4.1 Projected ERCs Calculation (optional) | [5 empty] | WS001 | A Spring |  | 90
|  | Total Projected ERCs | 447 |  |  | WS005 | B Well |  | 40
Existing Residential Connections |  |  | 400 |  |  | WS007 | next town wholesale |  | 50
Obligated Future ERCs (enter below) |  |  | 47
Example 1 Subdivision |  |  | 60
Example 2 Homes |  |  | 18
Example 3 Estates |  |  | 9
Another Example Place |  |  | 50
Serendipity Stable |  |  | 5
River of No Return |  |  | 46
Rock School |  |  | 12
[6 empty] | Maximum ERCs (assuming indoor use only) |  |  | 324
4.3 Summary - Existing Storage Tanks (enter below)
[8 empty] | Total Existing Storage Cap. (in gallons) | 140000
[6 empty] | ST001 | South Tank |  | 50000
[6 empty] | ST002 | Jones Tank |  | 90000
(Enter notes here. If additional space is needed, click the "Additional Notes" tab on the bottom of the screen.)
Yes
No
Yes
No
Enter number of non-residential connections, e.g., 2 industrial connections.
.
Convert "Number of other connections" (Cell E9) to ERCs here. [ERCs of other connections = peak day demand of other connections in gal per day / 800 gpd]
Enter estimated irrigated acre per residential lot here.
Enter total irrigated acres of other connections here.
Enter fire flow in gpm.
Enter duration in hours.
Autolink to 4.2 "Total Existing Source Capacity" cell below.
Select Irrigated Zone # from the pick list. See "Irrigation Demands & Map" tab on the bottom of the screen or WaterLink.
Autolink to 4.3 "Total Existing Storage Capcity" cell below.
If applicable, enter number of people per camp site here.
Less than 100% indicates: (1) additional source capacity is needed, and (2) source deficiency should be assessed.
Storage deficit indicates that: (1) additional storage volume is needed, and (2) storage deficiency should be assessed.
Use this number in Cell I8 ("Number of residential connections") on Page 1 to calculate PROJECTED demand & req'ts (including both existing & future connections).
Diaphragm or air pressure tanks shall NOT be considered effective storage volume for (1) community systems, or (2) NTNC with significant demand UNLESS an exception has been granted.
Autolink to 2 "Total Source" cell above.
Autolink to 2 "Total Storage" cell above.
If applicable, use this number in cell I8 or cell I9 on Page 1.
If NO, answer one of question set 2.01 to 2.05 in ESS.
If YES, answer one of question set 2.06 to 2.10 in ESS.
Less than 100% indicates: (1) additional storage capacity is needed, and (2) storage deficiency should be assessed.
Source deficit indicates that: (1) additional source capacity is needed, and (2) source deficiency should be assessed.

## Additional Notes
Additional Notes
System Name: | ABC Water System | System Number: | 09999
(Enter additional notes here, for example, water system information related to capacity calculations, etc.)

## Irrigation Demands & Map
Irrigation Demands & ERCs
(This reference table is used to automate the calculations in the PWS Capacity Calculation sheet. Do not alter.)
System Name: |  | ABC Water System |  |  |  | System Number: | 09999
Zone | Peak Day | Avg Year | Storage | IRRIGATION DEMANDS
| Demand | Demand | Reqmt | (to be added to indoor and fire flow demands)
3 | 3.39 | 1.66 | 2528 |  |  | Avg. Yr. | Storage | Peak
[5 empty] | Peak Day | (ac-ft/yr | Requirement | Instantaneous
|  |  |  | zone | (gpm/irr. ac) | per irr. ac.) | (gal/irr. ac) | (gpm/irr. ac)
|  |  |  | 1 | 2.26 | 1.17 | 1782 | 4.52
|  |  |  | 2 | 2.8 | 1.23 | 1873 | 5.6
|  |  |  | 3 | 3.39 | 1.66 | 2528 | 6.78
|  |  |  | 4 | 3.96 | 1.87 | 2848 | 7.92
|  |  |  | 5 | 4.52 | 2.68 | 4081 | 9.04
|  |  |  | 6 | 4.9 | 3.26 | 4964 | 9.8