## Surface Water Checklist
Source Development - Surface Water |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-515-4(3) | Total source capacity ≥ system peak day demand
R309-515-4(4) | Source water meets water quality requirements of R309-200 with treatment
R309-515-4(5) & 5(2)(a) | New source analysis provided for contaminants listed in R309-515-4(5)
R309-515-4(6) | Identify water source as surface water, groundwater, or under the influence of surface water (UDI) for DDW determination
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
R309-515-5(1) | Source water can be treated by conventional surface water treatment or equivalent technique acceptable to Director
N/A | Project will resolve existing physical deficiencies
Pre-Design Submittals
R309-515-5(2)(a) | Chemical analyses required by R309-200 and described in R309-515-4(5) submitted
R309-515-5(2)(b)(i) | Survey of watershed shows possible future uses of impoundments or reservoirs
R309-515-5(2)(b)(ii) | Survey of watershed shows present DWQ stream classification
R309-515-5(2)(b)(ii) | Survey of watershed shows obstacles to reclassification of stream as 1C
R309-515-5(2)(b)(ii) | Survey of watershed shows degree of watershed control by owner or other agencies
R309-515-5(2)(b)(iii) | Survey of watershed assesses hazard to supply by accidental spills of materials that are toxic or harmful to treatment process
R309-515-5(2)(b)(iv) | Survey of watershed has sample results assessing microbio., phys., chemical, & radiological characteristics/variations of water
R309-515-5(2)(b)(v) | Survey of watershed assesses capability of proposed treatment process to reduce contaminants to applicable standards
R309-515-5(2)(b)(vi) | Survey of watershed considers currents, wind, ice, and effect of tributary streams at their confluence
Pre-Construction Submittals
R309-515-5(3)(a) | Evidence provided that water system has legal right to divert water for proposed use
R309-515-5(3)(b) | Minimum quantity that source is capable of producing provided
R309-515-5(3)(c) | Plans, specs, & supporting docs submitted for treatment facilities to determine compliance with R309-525 or R309-530
Source Water Quantity
R309-515-5(4)(a) | Max. quantity assumed as ≤ low flow in 25-year recurrence interval or low flow of record if 25 years of records not available
R309-515-5(4)(b) | Source quantity will meet peak day demand per R309-510-7 and provide reasonable surplus for anticipated growth
R309-515-5(4)(c) | Source quantity will be adequate to compensate for all losses anticipated during normal operation (silting, evap., seepage)
Diversion Structures
R309-515-5(5)(a) | If water quality varies by depth, intake structure allows withdrawal of water from multiple levels
R309-515-5(5)(b) | Lowest intake level will stay submerged at low water elevation of the reservoir
R309-515-5(5)(c) | Separate facilities provided for release of less desirable water held in storage
R309-515-5(5)(d) | Design provides for cleaning of inlet line
R309-515-5(5)(e) | Diversion device provided to prevent large quantities of fish or debris from entering intake structure
R309-515-5(5)(f) | Suitable protection provided for pumps used to transfer diverted water
Impoundments
R309-515-5(6)(a) | Design of impoundment provides for removal of brush and trees to high water level
R309-515-5(6)(b) | Design provides for protection from floods during construction
R309-515-5(6)(c) | Design provides for abandonment of wells that will be inundated after construction of the impoundment
R309-515-5(6)(d) | Adequate precautions provided to limit nutrient loads