## Well Checklist
Source Development - Wells |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-515-4(3) | Minimum of 2 sources provided (community water systems with >100 connections and no surface water treatment)
R309-515-4(3) | Total source capacity ≥ system peak day demand
R309-515-4(4) | Source water meets water quality requirements of R309-200 (with treatment if required)
R309-515-4(5) | New source analysis provided for contaminants listed in R309-515-4(5)
R309-515-4(6) | Identify water source as surface water, groundwater, or under the influence of surface water (UDI) for DDW determination
R309-515-5(1) & 6(1) | For surface water or UDI source, identify whether surface water treatment of well water is provided (after well development)
R309-520-6(3)(b) | For groundwater, identify whether disinfection or inorganics treatment is needed and provided
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
N/A | Project will resolve existing physical deficiencies
Standby Power
R309-515-6(2)(b) | One or more sources equipped with redundant power supply or power supply from two independent substations
R309-515-6(2)(a) | Pre-lube line for pump-bearings has valved bypass or automatic control wired to emergency power source (auto pre-lube)
Utah Division of Water Rights
R309-515-6(3) | Well driller has start card from State Engineer's Office before beginning drilling [Drilling Requirement]
R309-515-6(3) | R655-4 (Water Wells) rules followed [Drilling Requirement]
Source Protection
R309-515-6(4) | Well location based on R309-600 requirements
R309-515-6(4) | Well located in area that minimizes threats from existing or potential pollution sources
R309-515-6(4) | Sewer lines absent from source protection zones 1 and 2 unless precautions are taken (see precautions below)
Source Protection - Precautions for Locating Sewer Lines in Zones 1 and 2
R309-515-6(4) | Sewer lines meet conditions of R309-600-13(3)
R309-515-6(4)(a) | Sewer lines constructed to remain watertight
R309-515-6(4)(a) | Sewer lines deflection tested per R317-3
R309-515-6(4)(a) | Sewer lines video-inspected before placing into service
R309-515-6(4)(a)(i) | HDPE sewers: PE3408 or PE4710, DR ≤17, with fusion-welded joints
R309-515-6(4)(a)(ii) | PVC sewers: C900 or C905, DR ≤18, restrained-gasket or fusion-welded joints, ID'd as sanitary sewer (no solvent cement joints)
R309-515-6(4)(a)(iii) | Ductile iron sewers: with ceramic epoxy lining, polyethylene encasement, restrained joints, and 200 min. pressure class
R309-515-6(4)(b) | Procedures for leakage tests per R317-3 specified
R309-515-6(4)(c) | Lateral to main connections fusion-welded, shop-fabricated, or with mechanical clamping watertight saddle
R309-515-6(4)(d) | Inlet and outlet sewer pipes joined to a manhole with flexible water-tight gasket
R309-515-6(4)(e) | Sewer pipe laid with max. 2% deflection at any joint
R309-515-6(4)(f) | Sewer pipe backfill compacted to at least 95% of max. lab density per ASTM D-690
R309-515-6(4)(g)(i) | Sewer manholes constructed of reinforced concrete
R309-515-6(4)(g)(ii) | Sewer manhole base and walls up to a min. of 12” above top of upper-most sewer pipe constructed in single pour wo/ joints
R309-515-6(4)(g)(iii) | Sewer manholes air-pressure tested after installation
R309-515-6(4)(h) | Unprotected aquifers: impermeable cutoff wall constructed in all sewer trenches up-gradient of zone 2
R309-515-6(4)(h) | Protected aquifers: impermeable cutoff wall constructed in all sewer trenches up-gradient of zone 1
Well Approval Process
R309-515-6(5)(a)(i) | Preliminary Evaluation Report submitted and acceptable before beginning well drilling
R309-515-6(5)(a)(ii) | Plan Approval given by DDW before beginning well drilling
R309-515-6(5)(c)(i) | Prior to use of new well, provide report of Well Driller stamped as received by State Engineer’s Office
R309-515-6(5)(c)(ii) | Prior to use of new well, provide well grouting approval letter
R309-515-6(5)(c)(iii) | Prior to use of new well, provide aquifer drawdown test data, w/yield vs. drawdown & comments/interpretation by PE or PG
R309-515-6(5)(c)(iv) | Prior to use of new well, provide chemical analysis required by R309-515-4(5) [new source analyses]
R309-515-6(5)(c)(v) | Prior to use of new well, provide evidence that owner has legal right to divert water from the well
R309-515-6(5)(c)(vi) | Prior to use of new well, provide plans and specifications by a PE for well house, equipment, and piping
R309-515-6(5)(c)(vii) | Prior to use of new well, provide bact. analysis of water after installation of permanent equipment, disinfection, and flushing
R309-515-6(5)(d) | Obtain an Operating Permit before introducing well water into water system
Well Materials, Design, and Construction - General
R309-515-6(6)(a) | Interior surfaces in contact with drinking water comply with ANSI/NSF 61
R309-515-6(6)(a) | Drop pipes, well screens, coatings, adhesives, solders, fluxes, pumps, switches, electrical wire, sensors meet ANSI/NSF 61
R309-515-6(6)(a) | All substances introduced to well during construction/development, incl. drilling fluids and regenerants, meet ANSI/NSF 60
Well Materials, Design, and Construction - Permanent Steel Casing
R309-515-6(6)(b)(i) | Casing is new and meets AWWA Standard A-100, ASTM, or API specifications in R655-4-11.2.3, Table 6
R309-515-6(6)(b)(ii) | Casing has additional thickness and weight provided if min. isn’t sufficient to assure reasonable life expectancy of the well
R309-515-6(6)(b)(iii) | Casing is capable of withstanding expected forces
R309-515-6(6)(b)(iv) | Casing is equipped with a drive shoe, if driven
R309-515-6(6)(b)(v) | Casing has full circumferential welds or threaded coupling joints
R309-515-6(6)(b)(vi) | Casing is min. of 18” above ground surface or 12” above pump house floor
R309-515-6(6)(b)(vi) | Top of casing terminates min. of 3’ above higher of 100-year flood level or highest known flood elevation at sites that flood
Well Materials, Design, and Construction - Non-Ferrous Casing
R309-515-6(6)(c) | Use of non-ferrous casing has received approval by Director
R309-515-6(6)(c) | Thermoplastic well casing meets AWWA Standard A100-06 and bears NSF-wc logo for compliance with NSF 14 for well casing
Well Materials, Design, and Construction - Disposal of Cuttings
R309-515-6(6)(d) | Cuttings and waste from well drilling not discharged to a waterway, lake, or reservoir
R309-515-6(6)(d) | Division of Water Quality rules for discharges followed
Well Materials, Design, and Construction - Packers
R309-515-6(6)(e) | Packer material does not impart taste, odor, toxic substances, or bacteria to well water
R309-515-6(6)(e) | Packers that contain lead are prohibited
Well Materials, Design, and Construction - Screens
R309-515-6(6)(f)(i) | Screen material resistant to chemical action of groundwater and cleaning operations
R309-515-6(6)(f)(ii) | Size of screen openings based on sieve analysis of formations or gravel pack materials
R309-515-6(6)(f)(iii) | Screen diameter sufficient to provide adequate specific capacity and low aperture entrance velocities
R309-515-6(6)(f)(iv) | Operating water level remains above the screen under all pumping conditions
R309-515-6(6)(f)(v) | Bottom plate or wash-down bottom fitting is made of the same material as the screen
Well Materials, Design, and Construction - Plumbness and Alignment
R309-515-6(6)(g) | Well tested for plumbness and vertical alignment per AWWA Standard A100
R309-515-6(6)(g)(i) | Test method and allowable tolerances for plumbness and vertical alignment clearly stated in specs
R309-515-6(6)(g)(ii) | Specs clearly indicate options that design engineer has if well fails to meet requirements for plumbness or vertical alignment
Well Materials, Design, and Construction - Casing Perforations
R309-515-6(6)(h)(i) | Perforations located to permit uniform collection of water around circumference of well casing
R309-515-6(6)(h)(ii) | Perforations are of dimensions and size to restrain water bearing soils from entering the well
Well Materials, Design, and Construction - Well Sealing
R309-515-6(6)(i) | Annulus between outermost well casing and borehole wall grout sealed min. of 100’ BGS (unless exception issued)
R309-515-6(6)(i) | More than one casing: annulus between outermost casing and inner casing grout-sealed or water-tight welded steel ring
R309-515-6(6)(i) | For wells with pitless adaptors, well sealed to a min. depth of 110’
R309-515-6(6)(i)(i)(A) | Annular opening allows min. of 2” of grout between outermost permanent casing and drilled hole
R309-515-6(6)(i)(i)(B) | Casing placed to permit unobstructed flow and uniform thickness of grout
R309-515-6(6)(i)(ii)(A) | Neat cement grout to seal 2” annulus opening conforms to ASTM Standard C150 with max. of 6 gallons of water/cement sack
R309-515-6(6)(i)(ii)(A) | Neat cement grout additives to increase fluidity are approved by Director
R309-515-6(6)(i)(ii)(B) | Concrete grout: annulus >2” may use equal parts cement (ASTM C150) and sand w/ max. 6 gal. of water/cement sack
R309-515-6(6)(i)(ii)(C) | Clay seal: for annulus openings >6” use of swelling bentonite seal meeting requirements of R655-4-11.42 approved by Director
R309-515-6(6)(i)(iii)(A) | Annular openings <4” – grout installed under pressure with a positive displacement pump from bottom of annular opening
R309-515-6(6)(i)(iii)(B) | Annular openings ≥4”/≤100’ deep: concrete grout gravity-placed, continuous operation, w/ pipe at bottom of opening
R309-515-6(6)(i)(iii)(C) | Temporary construction casings removed prior to or during well sealing (exceptions approved by SEO & submitted to Director)
R309-515-6(6)(i)(iii)(D) | Well in a protected aquifer sealed from ground surface to min. of 100’ below surface and through protective clay layer
R309-515-6(6)(i)(iii)(E) | After well is grouted, work on well discontinued until grout has properly set (usually 72 hrs)
Well Materials, Design, and Construction - Water Entering Well During Construction
R309-515-6(6)(j) | Water that enters the well during construction will be obtained from chlorinated water system
R309-515-6(6)(j) | If impossible to get water from chlorinated water system, treat water to produce 100 mg/L free chlorine per R655-4-11.6.5
Well Materials, Design, and Construction - Gravel Pack Wells
R309-515-6(6)(k)(i) | Gravel pack material made of well-rounded particles
R309-515-6(6)(k)(i) | Gravel pack material is min. 90% siliceous material
R309-515-6(6)(k)(i) | Gravel pack material is max. 5% acid solubility
R309-515-6(6)(k)(i) | Gravel pack material is smooth
R309-515-6(6)(k)(i) | Gravel pack material is uniform
R309-515-6(6)(k)(i) | Gravel pack material is free of foreign material
R309-515-6(6)(k)(i) | Gravel pack material is properly sized
R309-515-6(6)(k)(i) | Gravel pack material is washed
R309-515-6(6)(k)(i) | Gravel pack material is disinfected immediately prior to or during placement
R309-515-6(6)(k)(ii) | Gravel pack placed in one uniform, continuous operation
R309-515-6(6)(k)(iii) | Refill pipe is sch. 40 steel pipe incorporated in pump foundation
R309-515-6(6)(k)(iii) | Refill pipe terminates w/ screwed or welded cap, min. of 12” above pump house floor or concrete apron
R309-515-6(6)(k)(iv) | Refill pipes in grouted annular opening surrounded by min. of 1.5” of grout
R309-515-6(6)(k)(v) | Protection provided to prevent leakage of grout into gravel pack or screen
R309-515-6(6)(k)(vi) | Casings not removed meet requirements of R309-515-6(6)(b) or R309-515-6(6)(c)
Well Materials, Design, and Construction - Well Development
R309-515-6(7)(a) | Well developed to remove native silts and clays, drilling mud, or finer fraction of gravel pack
R309-515-6(7)(b) | Well development to continue until max. specific capacity is obtained
R309-515-6(7)(c) | Chemical conditioning: specs have method, equipment, chemicals, residual chemical testing, & disposal of waste & inhibitors
R309-515-6(7)(d) | Blasting procedures: specs include provisions for blasting & cleaning to assure grouting and casing are not damaged
Well Materials, Design, and Construction - Capping Requirements
R309-515-6(8)(a) | Well securely capped per R655-4-14.1 until permanent equipment is installed
R309-515-6(8)(b) | Well protected from tampering and entrance of foreign materials during work progress
Well Materials, Design, and Construction - Well Abandonment
R309-515-6(9)(a) | Test well and groundwater sources to be permanently abandoned, are abandoned per R655-4-14
R309-515-6(9)(b) | Wells to be abandoned are sealed to prevent exchange of water between aquifers
R309-515-6(9)(b) | Wells to be abandoned are sealed with neat cement grout (preferred method)
R309-515-6(9)(b) | Fill materials other than cement grout or concrete are disinfected and free of foreign materials
R309-515-6(9)(b) | Cement grout or concrete applied through pipe, tremie, or bailer
Well Materials, Design, and Construction - Well Assessment
R309-515-6(10)(a) | Recomend: do step drawdown test to determine max. pumping rate for intake setting prior to required constant-rate test
R309-515-6(10)(b)(i) | Constant rate test required after well development and before permanent pump placement
R309-515-6(10)(b)(ii) | Constant rate test methods clearly indicated in specifications
R309-515-6(10)(b)(iii) | Test pump w/ pumping capacity in excess of desired design discharge rate when pumped against max. anticipated drawdown
R309-515-6(10)(b)(iv) | Provide for continuous pumping for min. of 24 hours or until stabilized drawdown has continued for a min. of 6 hours when pumped at a constant rate equal to the desired design discharge rate
R309-515-6(10)(b)(v)(A) | Provide capacity vs. head characteristics for test pump (pump curve)
R309-515-6(10)(b)(v)(B) | Provide static water level (in ft. to nearest 10th, measured form identified datum – usually top of casing)
R309-515-6(10)(b)(v)(C) | Provide depth of test pump intake
R309-515-6(10)(b)(v)(D) | Provide time and date for starting and ending test
R309-515-6(10)(b)(vi)(A) | For min. of 10 uniform time intervals for each log cycle of the graphic evaluation, record time in minutes since start of test
R309-515-6(10)(b)(vi)(B) | For min. of 10 uniform time intervals for each log cycle of the graphic evaluation, record actual pumping rate
R309-515-6(10)(b)(vi)(C) | For min. of 10 uniform time intervals for each log cycle of the graphic evaluation, record pumping water level in ft. to nearest 10th from same datum used for the static water level
R309-515-6(10)(b)(vi)(D) | For min. of 10 uniform time intervals for each log cycle of the graphic evaluation, record drawdown in ft. to nearest 10th
R309-515-6(10)(b)(vi)(E) | For min. of 10 uniform time intervals for each log cycle of the graphic evaluation, provide graphic evaluation on semi-log graph paper plotting drawdown measurements on an arithmetic scale at locations corresponding to time since starting test on logarithmic scale
R309-515-6(10)(b)(vii)(A) | Record time since stopping pump test in minutes at time intervals similar to those used during constant-rate pump test after end of constant-rate test until there are no changes in water level depth for a min. of 6 hours
R309-515-6(10)(b)(vii)(B) | Record depth to water level in ft. to nearest 10th measured from same datum used for pumping water level at time intervals similar to those used during constant-rate pump test after end of constant-rate test until there are no changes in water level depth for a min. of 6 hours
Well Materials, Design, and Construction - Safe Yield
R309-515-6(10)(c) | If aquifer drawdown test data indicates drawdown has stabilized, safe yield of well will be 2/3 of pumping rate used in constant-rate test (safe yield is used to determine permanent ERCs the well can support)
Well Materials, Design, and Construction - Well Disinfection
R309-515-6(11) | New, modified, or reconditioned well and pumping equipment disinfected per AWWA Standards C654-03 and A100-06 as modified by (i) and (ii), below, before placing into service
R309-515-6(11)(i) | Sufficient chlorine added for a min. of 50 ppm for all parts of the well and installed equipment
R309-515-6(11)(i) | Chlorine solution retained in well for a min. of 8 hours
R309-515-6(11)(ii) | Satisfactory bacteriological water sample obtained before use of water in PWS
Well Materials, Design, and Construction - Well Equipping for Naturally Flowing Wells
R309-515-6(12)(a)(i) | Discharge controlled by valves
R309-515-6(12)(a)(ii) | Permanent casing sealed by grout
R309-515-6(12)(a)(iii) | If erosion of confining bed adjacent to well appears likely, special protective construction specified by Director
Well Materials, Design, and Construction - Well Pumps
R309-515-6(12)(b)(i) | Design discharge rate of well pump does not exceed constant-rate aquifer drawdown test rate
R309-515-6(12)(b)(ii)(A) | Line-shaft pumps: Casing firmly connected to pump structure or inserted into recess extending min. 0.5” into pump base
R309-515-6(12)(b)(ii)(B) | Line-shaft pumps: Pump foundation & base designed to prevent fluids contacting joints between pump base & casing
R309-515-6(12)(b)(ii)(C) | Line-shaft pumps: Intake of well pump is a min. of 10’ below max. anticipated drawdown elevation
R309-515-6(12)(b)(ii)(D) | Line-shaft pumps: Avoid use of oil lubrication for pumps with intake screens less than 400’ deep
R309-515-6(12)(b)(iii)(A) | Submersible pumps: Casing top sealed to prevent entrance of water under vibration or movement of conductors or cables
R309-515-6(12)(b)(iii)(B) | Submersible pumps: Electrical cable firmly attached to riser pipe at min. of 20’ intervals
R309-515-6(12)(b)(iii)(C) | Submersible pumps: Well pump intake a min. of 10’ below max. anticipated drawdown elevation
Well Materials, Design, and Construction - Pitless Well Units and Adapters
R309-515-6(12)(c) | Restore surface seal integrity if excavation for pitless unit compromises surface seal
R309-515-6(12)(c) | Torch-cut holes in casing along neat lines closely following outline of pitless adapter
R309-515-6(12)(c) | Torch-cut holes completely filled with competent weld with burrs and fins removed prior to installation of pitless unit/adaptor
R309-515-6(12)(c)(i) | Below ground connection not submerged in water during installation
R309-515-6(12)(c)(ii) | Unit/adapter terminates at the higher of a min. of 18” above final ground elevation or 3’ above highest known flood elevation
R309-515-6(12)(c)(iii) | Have a label or certification indicating compliance with Water Systems Council Pitless Adpater Standard (PAS-97)
R309-515-6(12)(c)(iv) | Have suitable access to interior of casing to disinfect the well
R309-515-6(12)(c)(v) | Suitable sanitary seal/cover at casing upper terminal prevents entrance of fluids/contamination, esp. at electrical cable conn.
R309-515-6(12)(c)(vi) | Have access to measure static and pumped water levels in well
R309-515-6(12)(c)(vii) | Allow a min. of one check valve within the well casing
R309-515-6(12)(c)(viii) | Have a lockable cover or otherwise be protected from vandals or sabotage
R309-515-6(12)(c)(ix) | Shop-fabricated from point of connection with well casing to unit cap or cover
R309-515-6(12)(c)(x) | Be watertight
R309-515-6(12)(c)(xi) | Constructed of materials at least equivalent to the casing with compatible wall thickness
R309-515-6(12)(c)(xii) | Have threaded, flanged, or mechanical field connection joint to the lateral discharge from the pitless unit
R309-515-6(12)(c)(xiii) | Be threaded or welded to the casing (only field welding on the pitless unit allowed is the connection to the casing)
R309-515-6(12)(c)(xiv) | Have inside diameter as great as that of the well casing (≤12”)
Well Materials, Design, and Construction - Well Discharge Piping
R309-515-6(12)(d)(i) | Designed with low friction loss
R309-515-6(12)(d)(ii) | For above-ground discharge, control valves and appurtenances are above pump house floor
R309-515-6(12)(d)(iii) | Protected from entrance of contaminants
R309-515-6(12)(d)(iv) | Smooth-nose sample tap (1st), check valve, press. gauge, flow measure, & shut-off valve (last) unless naturally flowing well
R309-515-6(12)(d)(v) | For well that pumps directly into distribution system, air release valve is upstream of the check valve
R309-515-6(12)(d)(v) | Air release valve not required if trapped air can be pumped to waste before water is introduced into the distribution system
R309-515-6(12)(d)(vi) | Exposed piping valves and appurtenances protected from physical damage and freezing
R309-515-6(12)(d)(vii) | Anchored to prevent movement
R309-515-6(12)(d)(viii) | Protected from surge or water hammer
R309-515-6(12)(d)(ix) | Pump-to-waste line with min. 12” clearance from flood rim of sewer or storm drain
R309-515-6(12)(d)(ix) | Pump-to-waste line end downturned
R309-515-6(12)(d)(ix) | Pump-to-waste line end covered with #4 mesh corrosion-resistant screen
Well Materials, Design, and Construction - Water Level Measurement
R309-515-6(12)(e)(i) | Water levels can be measured in the completed well
R309-515-6(12)(e)(ii) | Permanent water level measuring equipment is made of corrosion resistant materials
R309-515-6(12)(e)(ii) | Permanent water level measuring equipment attached firmly to the drop pipe or pump column
R309-515-6(12)(e)(ii) | Permanent water level measuring equipment installed to prevent entrance of foreign materials
Well Materials, Design, and Construction - Observation Wells
R309-515-6(12)(f)(i) | Constructed according to requirements for permanent wells if to remain in service after completion of water supply well
R309-515-6(12)(f)(ii) | Protected at upper terminal to prevent entrance of foreign materials
Well Materials, Design, and Construction - Electrical Protection
R309-515-6(12)(g) | Electrical controls on pump motors sufficient to eliminate electrical problems due to phase shifts, surges, lightning, etc.
Well Materials, Design, and Construction - Well House Construction
R309-515-6(13) | Well house provided for above-ground motors (strongly recommended)
R309-515-6(13)(a) | Permanent well casing min. of 12” above pump house floor or concrete apron AND 18” above final ground surface
R309-515-6(13)(a) | Well casing in underground vault: drain to daylight sized to handle excess well flow
R309-515-6(13)(a) | Well casing in underground vault: surface water runoff directed away from vault access
R309-515-6(13)(b) | Floor surface a min. of 6” above final ground elevation
R309-515-6(13)(b) | Floor surface sloped to provide drainage
R309-515-6(13)(b) | Floor drains to daylight (unless highly impractical)
R309-515-6(13)(c) | Sites subject to flooding: earth berm ≥ 2’ above highest known flood elevation or other protection determined by director
R309-515-6(13)(d) | Top of well casing terminates at the higher of a min. of 3’ above 100-year flood level or highest known flood elevation
R309-515-6(13)(e) | Well house ventilated to assure adequate protection of equipment
R309-515-6(13)(e) | Well house heated to assure adequate protection of equipment
R309-515-6(13)(e) | Well house lighted to assure adequate protection of equipment
R309-515-6(13)(f) | Director requires fencing similar to that required around spring areas where necessary to protect water quality
R309-515-6(13)(g) | Access provided through well house roof or wall to service or replace well pump