## Membrane SWT Checklist
Membrane for Surface Water Treatment |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-530-4(1) | In addition to conventional surface water treatment (i.e. coagulation, sedimentation and filtration as outlined in R309-525), several alternative methods may also be suitable: Direct Filtration, Slow Sand Filtration, Membrane Filtration, and Diatomaceous Earth Filtration (informational)
R309-530-4(2) | Plans and specs for alternative treatment incorporate requirements from relevant sections of other drinking water engineering rules for the specified treatment method and where applicable include (a) through (j) below:
R309-530-4(2)(a) | Plant Siting (see R309-525-6)
R309-530-4(2)(b) | Pre-design Submittal (see R309-515-5(2))
R309-530-4(2)(c) | Plant Reliability (see R309-525-7)
R309-530-4(2)(d) | Color Coding and Pipe Marking (see R309-525-8)
R309-530-4(2)(e) | Chemical Addition (see R309-525-11)
R309-530-4(2)(f) | Miscellaneous Plant Facilities (see R309-525-17, particularly sub-section R309-525-17(1), Laboratory)
R309-530-4(2)(g) | Operation and Maintenance Manuals (see R309-525-19)
R309-530-4(2)(h) | Safety (see R309-525-21)
R309-530-4(2)(i) | Disposal of Treatment Plant Waste (see R309-525-23)
R309-530-4(2)(j) | Disinfection (see R309-520)
R309-530-4(3) & R309-560-8(8)(a) | Source water quality data submitted before or with the plans and specifications
R309-530-4(3)(c) | Source water quality data contains: alkalinity, pH, temp, TOC, TSS, turbidity, and any other parameter necessary
N/A | Project will resolve existing physical deficiencies
Turbidity Limits
R309-200-5(5)(a)(ii) | The membrane treatment plant does not exceed the turbidity limit of 0.1 NTU for 95% of turbidity measurements
R309-200-5(5)(a)(ii) | The membrane treatment plant does not exceed the maximum turbidity limit of 0.5 NTU
Challenge Testing Requirements
R309-530-8(4)(a) | Proposed membrane has either NSF/ANSI 419 certification or accepted in another state.
R309-530-8(4)(b) | Challenge test was submitted to the Division
R309-530-8(4)(c) | Maximum LRV credits are proposed
R309-530-8(4)(d) | Maximum LRV credits can be demonstrated in a DIT
Pilot Testing Requirements
R309-530-8(5) | Pilot test will be completed for proposed membrane module or approval was granted by the Division to use operational data from a comparable full-scale membrane facility.
R309-530-8(6)(a) | Prior to conducting pilot testing, the Division has issued written concurrence with the pilot test protocol
R309-530-8(6)(b)(i) | The pilot test protocol specificies the source of water for the test.
R309-530-8(6)(b)(ii) | The pilot test protocol specificies the membrane module to be tested.
R309-530-8(6)(b)(iii) | The pilot test protocol specificies the number of modules to be tested.
R309-530-8(6)(b)(iv) | The pilot test protocol specificies the test duration, including the number of clean in place cycles.
R309-530-8(6)(b)(v) | The pilot test protocol specificies the time of year.
R309-530-8(6)(b)(vi) | The pilot test protocol specificies the objective of the test, including optimizing flux, productivity, backwash frequency, maintenance-clean frequency, and clean in place frequency.
R309-530-8(6)(b)(vii) | The pilot test protocol specificies the hydraulic configuration.
R309-530-8(6)(b)(viii) | Continuous monitoring for each module includes: elasped run time, pressure (feedwater, filtrate, and concentrate), flow (feedwater, filtrate, and concentrate), and tempurature (feedwater or filtrate).
R309-530-8(6)(b)(ix) | Water quality monitoring of the feedwater, filtrate, and concentrate including the parameters and sample frequency.
R309-530-8(6)(b)(x) | Details are included about the backwash process, including chemcial enhancement and sample frequency.
R309-530-8(6)(b)(xi) | Details are included about the maintenance cleaning process.
R309-530-8(6)(b)(xii) | Details are included about the clean-in-place process including the data collection and DIT before returning to service
R309-530-8(6)(b)(xiii) | Details are included about the direct integrity testing process and data collection
R309-530-8(6)(b)(xiv) | Details are included about the indirect integrity monitoring process and data collection
R309-530-8(6)(b)(xv) | Identify any prescreens before filter module
R309-530-8(6)(b)(xvi) | Identifies any pretreatment required for module efficacy
R309-530-8(6)(b)(xvii) | Identifies any post-treatment required
R309-530-8(6)(b)(xviii) | Details are included about waste disposal.
Preliminary Design Report (PDR)
R309-530-8(7)(a) | Prior to submitting plans and specifications, the Division has issued written concurrence with the preliminary design report
R309-530-8(7)(b)(i) | The PDR summarizes the pilot test results or comparable operational data addressing R309-530-8(6)
R309-530-8(7)(b)(ii)(A) | PDR specifies membrane filtration: flux operating Range
R309-530-8(7)(b)(ii)(B) | PDR specifies membrane filtration: differntial pressure
R309-530-8(7)(b)(ii)(C) | PDR specifies membrane filtration: Recovery flow
R309-530-8(7)(b)(ii)(D) | PDR specifies membrane filtration: Productivity
R309-530-8(7)(b)(ii)(E) | PDR specifies membrane filtration: membrane fouling based on pilot results
R309-530-8(7)(b)(ii)(F) | PDR specifies membrane filtration: membrane removal efficiency LRV, verified duirng pilot
R309-530-8(7)(b)(ii)(G) | PDR specifies membrane filtration: total membrane area per module
R309-530-8(7)(b)(ii)(H) | PDR specifies membrane filtration: number of membranes per module
R309-530-8(7)(b)(iii) | Treatment objectives based on source water quality including disinfection by product production and corrosivity of produced water
R309-530-8(7)(b)(iv) | PDR specifies the design capacity and basis
R309-530-8(7)(b)(v) | PDR specifies mode of filtration (constant flux or constant pressure)
R309-530-8(7)(b)(vi) | PDR specifies expected useful life of membranes
R309-530-8(7)(b)(vii) | PDR specifies critical componentts to be provided in duplicate to assure continuous operation
R309-530-8(7)(b)(viii) | Summary of Direct Integrity Testing
R309-530-8(7)(b)(ix) | Summary of Indirect Integrity Testing
Membrane Facility Design Requirements - Treatment Capacity
R309-530-8(8)(b)(i) | A membrane facility in a community system that is the sole source of water shall be capable of meeting the peak day demand at the lowest feedwater temp when the largest membrane is out of service by either: providing one redundant unit, or having multiple membrane unites with excess treatment capacity at the max design flux.
R309-530-8(8)(b)(ii) | A membrane facility in a noncommunity system that is the sole source of water and can shut down does not need to meet peak day demand when the largests membrane unit is out of service.
R309-530-8(8)(b)(iii) | The treatment capcacity accounts for: use of filtrate for backwashing and chemical cleaning, loss of concentrate, and loss of filtrate from flushing membranes after a chemical clean.
Membrane Facility Design Requirements - Redundancy of Critical Components
R309-530-8(8)(c)(i) | A membrane facility in a community system that is the sole source of water shall provide critical components needed to maintain operation, as identified in the PDR, in duplicate.
R309-530-8(8)(c)(ii) | A membrane facility in a noncommunity system that is the sole source of water and can shut down does not need to provide criticial components in duplicate.
Membrane Facility Design Requirements - Certification of Chemcials and Components
R309-530-8(8)(d)(i) | All chemcials used in water treatment, including those used for clean modules and piping are NSF/ANSI 60 certified.
R309-530-8(8)(d)(ii) | All materials in contact with water during treatment are NSF/ANSI 61 certified.
Membrane Facility Design Requirements - Membrane Facility Housing
R309-530-8(8)(e)(i) | Membranes are house in a weatherproof structure
R309-530-8(8)(e)(ii) | Membrane facility is accessible when the facility will be active
R309-530-8(8)(e)(iii) | Membrane facilities are protected from flooding
R309-530-8(8)(e)(iv) | Membrane facilities are drained to prevent water accumulation
R309-530-8(8)(e)(v) | Membrane facilites are locked and secured to prevent vandalism and unauthorized entry
R309-530-8(8)(e)(vi) | Membrane facility is heated, cooled, and vented to protect the equipment
R309-530-8(8)(e)(vii) | If necessary, membrane facility is dehumidified
R309-530-8(8)(e)(viii) | Membrane facility is adequately lit.
R309-530-8(8)(e)(ix) | Membrane facility is sized and configured to allow for operation and maintenacne, including removing and replacing membrane units.
Membrane Facility Design Requirements - Pre and Post Treatment
R309-530-8(8)(f) | Prefiltration screening and treatment is based on source water quality, pilot testing, and preliminary design report recommendations.
R309-530-8(8)(f)(i) | Prefiltration screening removes particles and debris that may damage or plug a membrane.
R309-530-8(8)(f)(ii) | Chemicals used in pretreatment are compatible with the membrane material
R309-530-8(8)(f)(iii) | If a pretreatment process used polymer, the polymer carryover to the membrane is minimized.
R309-530-8(8)(f)(iv) | Equipment is provided to routinely test the effectiveness of the pretreatment process.
R309-530-8(8)(g) | Post-treatment is based on source water quality, pilot testing, and preliminary design report recommendations.
R309-530-8(8)(g)(i) | Equipment is provided fo the routine testing and compliance monitoring of a post-treatment process
R309-530-8(8)(g)(ii) | Requirements for disinfection following membrane filtration are specified in Rules R309-200, R309-210, R309- 215, and R309-520.
Membrane Facility Design Requirements - Bypass, Backwash, and Filter to Waste
R309-530-8(7)(b)(x)(A) & (B) & (C) | PDR Includes Triggers for Initiating a backwash and chemically enhanced backwash and their frequencies and duration
R309-530-8(8)(h)(i) | Untreated surface or ground water under the direct influence of surface water shall not bypass membrane filtration.
R309-530-8(8)(h)(ii) | Any water blended with membrane filtrate prior to distribution meets drinking water standards.
R309-530-8(8)(i) | Each membrane unit shall be equipped to allow filtrate to be sent to waste instead of distribution
R309-530-8(7)(b)(x)(G) & R309-530-8(8)(j) | Waste generated by membrane filtration (concentrate, filter-to-waste-backwash, and spent cleaning solution) is disposed of accoring to applicable regulations.
R309-530-8(7)(b)(x)(I) | Proper cross connection is equipped for chemically enhanced backwash.
R309-530-8(8)(k)(i) | Membrane that require backwash are equipped with backwashing equipment.
R309-530-8(7)(b)(x)(E) | Chemical supply for backwash is identified
R309-530-8(8)(k)(ii) | Pipes used for backwash are compatible with chemical used for chemically enhanced backwash
R309-530-8(8)(k)(iii) | Air used during backwash is filtered, dry, and oil-free
R309-530-8(7)(b)(x)(H) & R309-530-8(8)(k)(iv) | Recycled backwash is treated to remove solids and returned to the headworks of the treatment plant
R309-530-8(8)(k)(v) | Pumps used for backwash have either, a variable frequency drive, soft start and start capabilities, or slow opening and closing of automatic valves.
R309-530-8(8)(k)(vi) | Backwash flow is measured
R309-530-8(7)(b)(x)(D) & R309-530-8(8)(k)(vii)(A) | Membranes shall be backwashed with filtrate
R309-530-8(8)(k)(vii)(B) | Filtrate is produced in sufficient volumes to backwash and maintain rated plant capacity.
Membrane Facility Design Requirements - Clean in Place and Maintenace Cleans
R309-530-8(7)(b)(xi) & R309-530-8(8)(l) | Details of the maintenace clean and clean in place process for membranes requiring chemical cleaning
R309-530-8(8)(l)(ii) | Piping and pumps shall be compatible with the chemicals used for cleaning
R309-530-8(7)(b)(xi)(A) | Triggers for inititiating the process
R309-530-8(7)(b)(xi)(B) | Process Frequency
R309-530-8(7)(b)(xi)(C) and (D) | Chemical supply and list of chemicals for maintenance clean and clean in place
R309-530-8(7)(b)(xi)(E) | Heating Requirements for the Cleaning Solution
R309-530-8(7)(b)(xi)(F) and (H) | Description of cleaning solution recirculation and chemical recycling, if applicable.
R309-530-8(7)(b)(xi)(G) | Description of the soak cycle
R309-530-8(7)(b)(xi)(I) | Post clean in place verification that chemical concentrations were adequate.
R309-530-8(7)(b)(xi)(J) | Post clean in place requirements include: backwash or flush, direct integrity test, and proper disposal of the waste-stream and rinse water.
R309-530-8(7)(b)(xi)(K) & R309-530-8(8)(l)(iii) | Proper cross connection is equipped chemical cleaning to isolate chemicals from thefeedwater and filtrate during the cleaning process
R309-530-8(8)(iv) | Secondary containment for leaks and spills from a chemical storage tank shall be provided to protect the operator and equipment, and prevent release of chemicals to the environment
Membrane Facility Design Requirements - Direct Integrity Testing
R309-530-8(7)(b)(viii) & R309-530-8(8)(m)(i) | Direct Integrity testing for each integral membrane filtration unit descrption includes:
R309-530-8(8)(m)(i) | Equipment for Direct Integrity Testing is provided to detect potential breaches and record test results
R309-530-8(8)(m)(ii) | Equipment shall be capable of applying the DIT to membranes, seals, potting materials, valves, piping, and any other component that could result in contamination if the integrity were compromised.
R309-530-8(7)(b)(viii)(A) | Description of testing procedure
R309-530-8(7)(b)(viii)(B) & R309-215-15(18)(b)(iii) | Method of direct integrity testing, currently pressure or marker testing
R309-530-8(7)(b)(viii)(C) & R309-215-15(18)(b)(iii)(F) | Frequency of testing, currenlty required once per calendar day (NOT every 24 hours of run time)
R309-530-8(7)(b)(viii)(D) & R309-530-8(8)(m)(iii)(D) & R309-215-15(18)(b)(iii)(B) | Estimated resolution of the DIT (at most it can be 3 micrometers)
R309-530-8(7)(b)(viii)(E) & R309-215-15(18)(b)(iii)(C) | Estimated sensitivity of the DIT
R309-530-8(7)(b)(viii)(F) | For pressure based testing the calculations demonstrate how the measured pressure or flow is converted into an LRV
R309-530-8(7)(b)(viii)(I) | For pressure based testing: the baseline responsive, if applicable, and how it was determined.
R309-530-8(8)(m)(iii) | Air used pressure based testing is filtered, dry, and oil-free.
R309-530-8(7)(b)(viii)(G) | For marker based testing: idendification of marker and how marker will be discretely quantified or meausred.
R309-530-8(8)(m)(iv) | A particle used for marker based testing is NSF/ANSI 60 certified, inert, compatible with membrane material, has an effecitve size less than 3 micrometers, has a nuetral surface charge, can be discretely measured, and is removed less effectively that the organism targeted by the membrane filtration.
R309-530-8(8)(m)(v) | A molecule used for marker based testing is capable of discrete quanification and less than an effective size of 3 micrometers
R309-530-8(7)(b)(viii)(H) | Estimated control limits
R309-530-8(7)(b)(xi)(J)(II) | A DIT is performed after a maintenance clean or clean in place process.
Membrane Facility Design Requirements - Indirect Integrity Testing
R309-530-8(7)(b)(ix) | Indirect Integrity Monitoring of filtrate possible for each membrane unit including:
R309-530-8(7)(b)(ix)(A) | Description of the indirect integrity monitoring procedure
R309-530-8(7)(b)(ix)(B) & R309-215-15(18)(b)(iv) | Method of continuous indirect integrity monitoring (turbidity monitoring most common)
R309-530-8(7)(b)(ix)(C) & R309-215-15(18)(b)iv)(B) | Frequency of monitoring meeting the requirements (must be at least every 15 minutes)
R309-530-8(7)(b)(ix)(D) & R309-215-15(18)(b)(iv)(D) or (E) | Estimated performance-based control limit (for turbidity this is to stay below 0.15 NTU)
R309-530-8(7)(b)(ix)(E) & R309-215-15(18)(b)(iv)(D) or (E) | Triggers for initiating a DIT (if the turbidity is above 0.15 NTU for a period greater than 15 min, the skid must be taken offline and pass a DIT before coming back online)
Membrane Facility Design Requirements - Sample Collection
R309-530-8(8)(o) | Means to Collect Samples are provided at the:
R309-530-8(8)(o)(i) | Raw Water Inlet for the facility
R309-530-8(8)(o)(ii) | Feedwater inlets to a membrane unit
R309-530-8(8)(o)(iii) | Filtrate Outlet from a membrane unit
R309-530-8(8)(o)(iv) | Concentrate Outlet (if present)
R309-530-8(8)(o)(v) | Combined-Filter Effluent Outlet
R309-530-8(8)(o)(vi) | Finished-water outlet from the facility
R309-530-8(8)(o)(vii) | Water supply for membrane backwashing
R309-530-8(8)(o)(viii) | Clean-in-Place chemcial solution
Membrane Facility Design Requirements - Flow Measurement
R309-530-8(8)(p) | Means to measure and record the toatl flow and rate of flow provided at the:
R309-530-8(8)(p)(i) | Raw Water Inlet for the facility
R309-530-8(8)(p)(ii) | Feedwater inlets to a membrane unit
R309-530-8(8)(p)(iii) | Filtrate Outlet from a membrane unit
R309-530-8(8)(p)(iv) | Concentrate Outlet (if present)
R309-530-8(8)(p)(v) | Finished-water outlet from the facility
R309-530-8(8)(p)(vi) | Water supply for membrane backwashing
R309-530-8(8)(p)(vii) | Recyled Water
Membrane Facility Design Requirements - pH and Tempurature Measurement
R309-530-8(8)(q) | pH and Tempurate can be measured and recorded the following locations:
R309-530-8(8)(q)(i) | Raw-water inlet for the facility
R309-530-8(8)(q)(ii) | Finished-water outlet from the facility
Membrane Facility Design Requirements - Pressure Measurement
R309-530-8(8)(r) | Pressure can be measured and recorded for the membrane filtration unit at the following locations:
R309-530-8(8)(r)(i) | Feedwater inlet
R309-530-8(8)(r)(ii) | Concentrate Outlet (if present)
R309-530-8(8)(r)(iii) | Filtrate Outlet
Membrane Facility Design Requirements - Turbidty Measurement
R309-530-8(8)(s) | Turbidity can be measured and recorded at the following locations:
R309-530-8(8)(s)(i) | Raw-water inlet for the facility
R309-530-8(8)(s)(ii) | Outlet from a pretreatment process
R309-530-8(8)(s)(iii) | Filtrate outlet from individual membrane units
R309-530-8(8)(s)(iv) | Combined-Filter Effluent Outlet
R309-530-8(8)(s)(v) | Outlet from other post-filter process downstream of membrane units that may increase turbidity
R309-530-8(8)(s)(vi) & R309-215-9(1)(a) | Clearwell Outlet
Membrane Facility Design Requirements - Cross Connection Control
R309-530-8(8)(t) | Cross-connection control shall be provided to prevent contamination of feedwater and filtrate from cleaning chemicals and waste disposal
Membrane Facility Design Requirements - System Controls
R309-530-8(8)(u) | System controls for a membrane filtration facilty are:
R309-530-8(8)(u)(i)(A) | Located above ground
R309-530-8(8)(u)(i)(B) | Protected from flooding
R309-530-8(8)(u)(i)(C) | Capable of automatically shutting down the filtration process to prevent damage to the membranes or distribution of inadquately treated drinking water
R309-530-8(8)(u)(ii) | Automated system controls are provided with:
R309-530-8(8)(u)(ii)(A) | Spare input/output cards
R309-530-8(8)(u)(ii)(B) | Backup Power Supply
R309-530-8(8)(u)(ii)(C) | Surge Protection
Membrane Facility Design Requirements - Alarms
R309-530-8(8)(v) | A membrane filtration facility shall include an alarm system that immediately notifies a water system operator when:
R309-530-8(8)(v)(i) | Feedwater turbidity exceeds the maximum design level
R309-530-8(8)(v)(ii) & R309-200-5(5)(a)(ii) | Filtrate turbidity exceeds the level not to be exceeded at any time (currently 0.5 NTU for membrane filtration)
R309-530-8(8)(v)(iii) | A direct or indirect integrity test exceeds a control limit
R309-530-8(8)(v)(iv) | The maximum flow rate setting corresponding to the maximum design flux level is exceeded;
R309-530-8(8)(v)(v) | TMP exceeds the maximum design level
R309-530-8(8)(v)(vi) | A pump driving the filtration, backwashing, or chemical cleaning process fails
Membrane Facility Design Requirements - Control of Remote or Unoccupied Membrane Filtration Facilities
R309-530-8(8)(w)(i) | A remote or unoccupied membrane filtration facility shall be provided with alarms, communication systems, and the ability to automatically shut down processes to prevent the distribution of inadequately treated drinking water
R309-530-8(8)(w)(ii) | In addition to the items listed in Subsection R309-530-8(8)(v), a remote or unoccupied membrane filtration facility shall include an alarm system that immediately notifies a water system operator of:
R309-530-8(8)(w)(ii)(A) | failure of a critical component identified in the preliminary design report
R309-530-8(8)(w)(ii)(B) | failure of a programable logic controller
R309-530-8(8)(w)(ii)(C) | membrane unit shutdown
R309-530-8(8)(w)(ii)(D) | clearwell water level above the maximum or below the minimum
R309-530-8(8)(w)(ii)(E) | chlorine residual level above the maximum or below the minimum
R309-530-8(8)(w)(ii)(F) | low level in a chemical storage tank
R309-530-8(8)(w)(ii)(G) | loss of electrical power
R309-530-8(8)(w)(ii)(H) | unauthorized entry
R309-530-8(8)(w)(ii)(I) | low interior temperature of a treatment building
Membrane Facility Startup
R309-530-8(9)(a) | A membrane filtration facility shall be equipped to allow for disposal of feedwater and filtrate during the startup process
R309-530-8(9)(b)(i) | Prior to installing membrane modules pipes shall be flushed to remove dirt and construction debris
R309-530-8(9)(b)(ii) | Prior to membrane installation the chemcial feed equipment shall be tested to assure proper operation and proper chemical dose delivery
R309-530-8(9)(b)(iii) | Prior to membrane installation mechanical equipment shall be tested for leaks and proper operation
R309-530-8(9)(b)(iv) | Prior to membrane installation instrumentation shall be calibrated and tested for proper operation
R309-530-8(9)(b)(v) | Prior to membrane installation the control system shall be verified for digital and analog control inputs and outputs, alarm limits, programming logic, instrumentation loops,a nd operational sequences.
R309-530-8(9)(c)(i) | After membrane installation, the modules should be flushed to waste to remove storage solution
R309-530-8(9)(c)(ii) | After membrane installation, the modules are tested to assure smooth startup and shutdown
R309-530-8(9)(d) | A water supplier shall comply with applicable disposal requirements for waste flushed from newly installed piping, tanks, equipment, and membranes at a membrane filtration facility
R309-530-8(9)(e)(i) | Prior to use of the facility to provide drinking water, the facility is disinfected and flushed according to AWWA procedures
R309-530-8(9)(e)(ii) | Prior to use of the facility to provide drinking water, membranes are disinfected per manufacturer instructions
R309-530-8(9)(e)(iii) | Prior to use of the facility to provide drinking water, facility is operating continuously for a trail period to verify design parameters (typically four days)
R309-530-8(9)(e)(iv) | Prior to use of the facilty to provide drinking water, treated water quality shall be sampled and demonstrate compliance with drinking water standards
R309-530-8(9)(e)(v) | Prior to use of the facility to provide drinking water, final, operational control limits for direct integrity testing shall be established
R309-530-8(9)(e)(vi) | Prior to use of the facility to provide drinking water, a DIT shall be done per Subsection R309-215-15(18)(b)(iii), and the result may not exceed the established upper control limit
R309-530-8(9)(e)(vii) & R309-500-9 | Prior to use of the facility to provide drinking water, a water supplier shall obtain an operating permit
R309-530-8(9)(f) | A water supplier shall assure that adequate operator training and instruction are provided by the supplier of the membrane units on each aspect of startup and operation of a membrane filtration facility
Membrane Facilty Additional Requirements for Operating Permit
R309-530-8(10) | In addition to meeting the requirements for an operating permit in Section R309-500-9, a water supplier requesting an operating permit for a membrane filtration facility treating surface water or groundwater under the direct influence of surface water shall provide to the division
R309-530-8(10)(a) | a statement acknowledging that the facility startup requirements of Subsection R309-530-8(9) have been completed
R309-530-8(10)(b) | normalized operating flux range
R309-530-8(10)(c) | normalized operating flux per membrane unit
R309-530-8(10)(d) | maximum operating differential pressure for a membrane unit
R309-530-8(10)(d) | membrane unit backwashing frequency
R309-530-8(10)(f) | membrane unit clean-in-place frequency
R309-530-8(10)(g) | minimum, verified, operational, direct integrity testing resolution
R309-530-8(10)(h) | maximum, verified, operational, direct integrity testing sensitivity
R309-530-8(10)(i) | verified, operational, direct integrity testing control limit
R309-530-8(10)(j) | verified, indirect integrity monitoring performance-based upper control limit
Membrane Replacement
R309-530-8(12)(a) | A water supplier shall obtain plan approval and an operating permit for replacement of:
R309-530-8(12)(a)(i) | an approved membrane module with a different module
R309-530-8(12)(a)(ii) | an approved number of modules with a greater number of the same modules
R309-530-8(12)(b) | Replacement of a membrane module with exactly the same product is considered ongoing operation and maintenance and is not a public drinking water project that requires plan approval or an operating permit
Calibration of Instrumentation
R309-530-8(13) | Instrumentation used to verify operation of a treatment process or determine compliance with monitoring and reporting requirements for a drinking water rule, shall be:
R309-530-8(13)(a) | calibrated monthly
R309-530-8(13)(b) | tested for accuracy monthly
R309-530-8(13)(c) | maintained according to manufacturer's recommendations