## Water Tank Checklist
| Water Storage Tank |  |  |  |  | Utah DEQ |  | Yes
| Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water |  | No
N/A
| Project Information (to be completed by the applicant) |  | Professional Engineer Responsible for Design (to be completed by the design PE)
| PWS Name: |  | Name:
| PWS ID: |  | Registration No.:
| Project Description: |  | Phone No.:
Email:
Engineer's Certification:
By checking the following box, I certify that the information that I have provided
on this form is true and accurate to the best of my knowledge.
| DDW Plan Review Information (to be completed by DDW review engineer) |  | DDW Plan Review Workflow (to be completed by DDW review engineer)
| Project File Number: |  | Review completed and checklist below updated:
| Plan Review Engineer: |  | Written correspondence based on review sent to PWS:
Instructions: In the appropriate column below, orange for the Design Engineer and blue for DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
| UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
General Requirements
| R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
| R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
| R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
| R309-500-10 | Method of wastewater disposal approved by DWQ or LHD (new water systems/subdivision additions)
| N/A | Project will resolve existing physical deficiencies
Hydraulic Analysis
| R309-511-4 (1)(a)(i)(A-G) | Certification and hydraulic model report unnecessary (if project type is listed in R309-511-4 (1)(a)(i)(A-G)) |  |  |  | Note project type here
| R309-511-4 (1)(b) | Certification of hydraulic modeling results by PE provided (if project type is not listed in R309-511-4 (1)(a)(i)(A-G)) |  |  |  | Note reason here if answer is 'No'
| R309-511-4 (2)(d) | Hydraulic model report provided (unless R309-511-4 (1)(a)(ii-iv) exemptions apply)
| R309-511-4 (2)(f) | System capacity and expansion report provided in lieu of hydraulic model report (if required by the Director)
Tank Effect on Distribution System Pressure
| R309-545-7 (1) | Tank location provides minimum working pressures per R309-105-9 in distribution system |  |  |  |  | 0
| R309-105-9 (2)(a) | Minimum 20 psi peak day demand during fire flow
| R309-105-9 (2)(b) | Minimum 30 psi peak instantaneous demand
| R309-105-9 (2)(c) | Minimum 40 psi peak day demand
Size and Volume
| R309-545-5 | Storage tank sized to meet minimum storage volumes per R309-510 |  |  |  |  | 0
| R309-510-8 (1)(a)&(2)(a-c) | Equalization storage volume based on average day demand for indoor and outdoor use |  |  |  |  | 0
| R309-510-8 (1)(b)&(3) | Fire suppression storage volume based on local fire authority requirements or 120,000 gal. (systems with fire hydrants) |  |  |  |  | 0
| R309-510-8 (1)(c)&(4) | Emergency storage volume when required by the Director based on risk assessment |  |  |  |  | 0
Material and Structural Design
| R309-545-6 (1) | Tank material provides stability, durability, and protects water quality |  |  |  |  | 0
| R309-545-6 (1) | Steel tanks designed per AWWA D100-11 |  |  |  |  | 0
| R309-545-6 (2) | Structural design sufficient for tank location |  |  |  |  | 0
Site/Location
| R309-545-7 (2) | Tank elevation adequate to serve all present and anticipated future connections |  |  |  |  | 0
| R309-545-7 (3) | Tank located a minimum of 50 lateral feet from sewers |  |  |  |  | 0
| R309-545-7 (4) | Ground within 50 foot radius of tank graded to prevent standing water (ground-level & buried tanks) |  |  |  |  | 0
? | R309-545-7 (5) | Tank capable of being isolated from distribution system without loss of pressure or service in distribution system |  |  |  |  | 0
? | R309-545-7 (5) | Tank capable of being drained for cleaning and maintenance |  |  |  |  | 0
| R309-545-7 (6) | Potential geologic hazards of tank site evaluated |  |  |  |  | 0
| R309-545-7 (6) | Earthquake and landslide risks assessed |  |  |  |  | 0
| R309-545-7 (7) | Tank site and design considers tank security and potential for vandalism |  |  |  |  | 0
| R309-545-8 (1) | Base of ground-level or buried tank a minimum of 3 feet above 100-year or maximum known flood level |  |  |  |  | 0
| R309-545-8 (2) | Base of buried tank above level of ground water table |  |  |  |  | 0
Roofs, Sidewalls, and Appurtenances
| R309-545-8 (3) | Roof of earth-covered buried tank sloped to drain toward outside edge of tank |  |  |  |  | 0
| R309-545-9 (1) | Tank designed with watertight roof and sidewalls to exclude animals, insects, and dust |  |  |  |  | 0
| R309-545-9 (2) | Roof and sidewall penetrations kept to a minimum |  |  |  |  | 0
| R309-545-9 (2)(a) | Pipes penetrating roof/sidewall of metal tanks welded or gasketed |  |  |  |  | 0
| R309-545-9 (2)(a) | Pipes penetrating roof/sidewall of concrete tanks use standard wall castings w/seepage rings poured in place |  |  |  |  | 0
| R309-545-9 (2)(a) | Vent pipes on concrete tanks designed with seepage rings and raised curbs formed in single pour with roof deck |  |  |  |  | 0
| R309-545-9 (2)(a) | Tank penetrations solely for pipes carrying drinking water |  |  |  |  | 0
| R309-545-9 (2)(b) | Openings in roof for controls or pump columns welded or curbed and sleeved |  |  |  |  | 0
| R309-545-9 (3) | Minimum double wall separation provided between water and wastewater compartments |  |  |  |  | 0
| R309-545-9 (4) | Tank roof drainage designed to prevent water ponding |  |  |  |  | 0
| R309-545-9 (4) | Roof parapets and similar structures absent or designed with waterproofing and drainage |  |  |  |  | 0
| R309-545-9 (4) | Downspout and roof drain tank penetrations absent |  |  |  |  | 0
| R309-545-16 | Tank and appurtenances (e.g., risers, overflows, vents) designed to prevent freezing |  |  |  |  | 0
| R309-545-17 | Tank designed with level control devices to maintain water levels |  |  |  |  | 0
Drains
| R309-545-10 (1)(a) | Tank drain provided |  |  |  |  | 0
| R309-545-10 (1)(b) | Tank drain sloped for complete tank drainage |  |  |  |  | 0
| R309-545-10 (1)(b) | Tank drain separate from tank outlet |  |  |  |  | 0
| R309-545-10 (1)(c) | Tank drain separate from sanitary sewer |  |  |  |  | 0
| R309-545-10 (1)(d) | If discharge to storm drain is permitted, end of drain line a minimum of 12 inches above storm drain overflow rim |  |  |  |  | 0
Internal Features
| R309-545-10 (2) | Internal catwalks designed with solid floors and raised edges |  |  |  |  | 0
| R309-545-10 (3)(a) | Tank outlet pipe location provides a silt trap prior to discharge from tank |  |  |  |  | 0
| R309-545-10 (3)(b) | Inlet and outlet pipes configured to provide water mixing and circulation in tank |  |  |  |  | 0
| R309-545-10 (4) | Tank floor sloped to permit complete tank drainage |  |  |  |  | 0
Surfaces and Coatings
| R309-545-11 (1) | Specs require interior surfaces and coatings of all equipment in contact with drinking water to meet NSF/ANSI 61 |  |  |  |  | 0
| R309-545-11 (2)(a) | Specs require curing per manufacturer's requirements and prohibit filling tank until curing is complete |  |  |  |  | 0
| R309-545-11 (2)(b) | Specs prohibit tank coating or repair from causing MCL violations |  |  |  |  | 0
| R309-545-11 (2)(c) | Specs require cleaning, disinfection, and flushing prior to placing tank in service |  |  |  |  | 0
| R309-545-11 (2)(d) | Specs require VOC analysis of water prior to placing tank in service |  |  |  |  | 0
| R309-545-12 (1) | Painting/protective coating specified for outside and inside of steel tanks |  |  |  |  | 0
| R309-545-12 (2) | Cathodic protection designed and to be installed/maintained by person trained in corrosion engineering (steel tanks) |  |  |  |  | 0
Overflows
| R309-545-13 | Tank overflow discharges 12" to 24" above ground surface or rim of receiving basin |  |  |  |  | 0
| R309-545-13 | Tank overflow designed to direct discharge away from tank and to prevent erosion |  |  |  |  | 0
| R309-545-13 (1) | Overflow diameter sized to permit outflow in excess of filling rate |  |  |  |  | 0
| R309-545-13 (2) | Overflow sloped for complete drainage |  |  |  |  | 0
| R309-545-13 (3) | Overflow pipe screened with non-corrodible No. 4 mesh screen and at a location least susceptible to vandalism |  |  |  |  | 0
| R309-545-13 (4) | Overflow pipe located where discharge will be visible |  |  |  |  | 0
| R309-545-13 (5) | Overflow separate from sanitary sewer |  |  |  |  | 0
Access Openings
| R309-545-14 | Tank designed with reasonably convenient access for cleaning and maintenance |  |  |  |  | 0
| R309-545-14 (1) | Tank designed with at least one roof access opening above the overflow level |  |  |  |  | 0
| R309-545-14 (1) | Roof access opening on a non-buried tank designed to be framed a minimum of 4" above the roof surface |  |  |  |  | 0
| R309-545-14 (1) | Roof access opening on a buried tank designed to extend a minimum of 18" above the earthen cover
| R309-545-14 (1) | Frame for roof access opening designed to be securely fastened and sealed to prevent inflow of contaminants |  |  |  |  | 0
| R309-545-14 (1) | Access openings on concrete tanks designed with sloped raised curbs poured continuously with the roof |  |  |  |  | 0
| R309-545-14 (2) | Shoebox type lid on access opening with 2" overhang around frame, gasket, & no surface penetrations |  |  |  |  | 0
| R309-545-14 (3) | Access opening lid designed with lock |  |  |  |  | 0
Vents
| R309-545-15 | Tank designed with vent; vent capacity exceeds water inflow and water outflow |  |  |  |  | 0
| R309-545-15 (1) | Vent inverted - downturned a minimum of 2" below any opening; vent shielded |  |  |  |  | 0
| R309-545-15 (2) | Vent discharge point a minimum of 24" above earthen cover on buried tanks |  |  |  |  | 0
| R309-545-15 (3) | Vent located and sized to prevent blockage during winter |  |  |  |  | 0
| R309-545-15 (4) | Vent designed with non-corrodible No. 14 (or finer) mesh screen |  |  |  |  | 0
| R309-545-15 (5) | Vent 6" or greater in diameter designed with additional heavy gage screen to protect fine mesh screen |  |  |  |  | 0
Safety
| R309-545-18 (1) | Tank designed with appropriate personnel safety devices (per Utah OSHA at a minimum) |  |  |  |  | 0
| R309-545-18 (2) | Ladder greater than 20' long designed with appropriate safety features (cage, harness, platform, etc.) |  |  |  |  | 0
| R309-545-18 (3) | Elevated tank designed with railings/handholds to access tank interior |  |  |  |  | 0
Disinfection
| R309-545-19 | Specs require cleaning and disinfection of new tank per AWWA C651-11 prior to being placed in service |  |  |  |  | 0
| R309-545-19 | Specs require proper disposal of super-chlorinated water from tank per UAC R317 |  |  |  |  | 0
Standards
| R309-545-20 (1)(a) | Specs incorporate AWWA C652-11, Disinfection of Water Storage Facilities |  |  |  |  | 0
| R309-545-20 (1)(b) | Specs incorporate AWWA D100-11, Welded Carbon Steel Tanks for Water Storage |  |  |  |  | 0
| R309-545-20 (1)(c) | Specs incorporate AWWA D102-11, Coating Steel Water-Storage Tanks |  |  |  |  | 0
| R309-545-20 (1)(d) | Specs incorporate AWWA D103-09, Factory-Coated Bolted Carbon Steel Tanks for Water Storage |  |  |  |  | 0
| R309-545-20 (1)(e) | Specs incorporate AWWA D104-11, Automatically Controlled, Impressed-Current Cathodic Protection… |  |  |  |  | 0
| R309-545-20 (1)(f) | Specs incorporate AWWA D110-13, Wire and Strand-Wound, Circular, Prestressed Concrete Water Tanks |  |  |  |  | 0
| R309-545-20 (1)(g) | Specs incorporate AWWA D115-06, Tendon-Prestressed Concrete Water Tanks |  |  |  |  | 0
| R309-545-20 (1)(h) | Specs incorporate AWWA D120-09, Thermosetting Fiberglass-Reinforced Plastic Tanks |  |  |  |  | 0
| R309-545-20 (1)(i) | Specs incorporate AWWA D130-11, Geomenbrane Materials for Potable Water Applications |  |  |  |  | 0
| R309-545-20 (2)(a) | Specs incorporate NSF 60, Drinking Water Treatment Chemicals - Health Effects |  |  |  |  | 0
| R309-545-20 (2)(b) | Specs incorporate NSF 61, Drinking Water System Components - Health Effects |  |  |  |  | 0
| R309-545-20 (3) | Specs incorporate applicable standards of Utah Occupational Safety and Health Division |  |  |  |  | 0
Inspection, Cleaning, and Repair
| R309-545-21 (1) | Specs require tanks entered for cleaning/inspection to be disinfected per AWWA C652-11 prior to return to service |  |  |  |  | 0
| R309-545-21 (2) | Specs require material for recoating/repairing of tank interior to be certified to meet NSF 61 |  |  |  |  | 0
| R309-545-21 (2) | Specs require material for underwater recoating/repairing of tank interior be suitable for underwater application |  |  |  |  | 0
| R309-545-21 (2) | Specs require material for underwater recoating/repairing of tank interior to be certified to meet NSF 60 & 61 |  |  |  |  | 0
Engineer's Certification
Yes
Yes