## Spring Checklist
Source Development - Springs |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-515-4(3) | Minimum of 2 sources provided (community water systems with >100 connections and no surface water treatment)
R309-515-4(3) | Total source capacity ≥ system peak day demand
R309-515-4(4) | Source water meets water quality requirements of R309-200 (with treatment if required)
R309-515-4(5) & 7(4)(e) | New source analysis provided for contaminants listed in R309-515-4(5)
R309-515-4(6) | Identify water source as surface water, groundwater, or under the influence of surface water (UDI) for DDW determination
R309-515-5(1) & 7(1) | For surface water or UDI source, identify whether surface water treatment of spring water is provided.
R309-520-6(3)(b) | For groundwater, identify whether disinfection or inorganics treatment is needed and provided.
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
N/A | Project will resolve existing physical deficiencies
Source Protection
R309-515-7(2) | Spring located to minimize threats from existing or potential sources of pollution
R309-515-7(2) | Preliminary Evaluation Report for source protection provided per R309-600-13(2)
R309-515-7(2) | Sewer lines and manholes within source protection Zones 1 & 2 approved by Director and designed per R309-515-6(4)
Pre-Construction
R309-515-7(4)(a) | Detailed plans and specifications provided
R309-515-7(4)(b)(i) | Engineer's or geologist's statement of historical spring flow variation provided if available
R309-515-7(4)(b)(ii) | Engineer's or geologist's statement of minimum flow and time of annual occurrence provided if available
R309-515-7(4)(b)(iii) | Engineer's or geologist's statement of maximum flow and time of annual occurrence provided if available
R309-515-7(4)(b)(iv) | Engineer's or geologist's statement of expected average flow provided if available
R309-515-7(4)(b)(v) | Engineer's or geologist's statement of spring behavior during drought provided if available
R309-515-7(4)(f) | Assessment of whether the spring is UDI per site inspection, geological condition, MPA, or chemical analysis |  |  |  | Specify method of assessment
Information Required after Spring Development & Redevelopment
R309-515-7(5)(a) | Proof of satisfactory bacteriologic quality
R309-515-7(5)(b) | 3 years of monthly flow data collected during operating seasons when spring is accessible
R309-515-7(5)(c) | Record drawings for developed spring
Spring Development
R309-515-7(7)(a) | Min. of 10' of impervious soil cover placed at least 15' laterally in all directions from spring collection device specified
R309-515-7(7)(a) | Clean, inert, non-organic material specified in the vicinity of the collection device
R309-515-7(7)(b)(i) | Alternative to impervious soil cover: impermeable liner of at least 40 mils thickness specified
R309-515-7(7)(b)(ii) | Alternative to impervious soil cover: liner seams specified as folded or welded to prevent leakage
R309-515-7(7)(b)(iii) | Alternative to impervious soil cover: liner specified to meet ANSI/NSF 61 if contact with drinking water will occur
R309-515-7(7)(b)(iv) | Alternative to impervious soil cover: specifications prohibit stones ≥ 2" or with sharp edges within 2" of liner
R309-515-7(7)(b)(v) | Alternative to impervious soil cover: min. of 2' of imperious soil cover over liner specified
R309-515-7(7)(b)(vi) | Alternative to impervious soil cover: liner and soil cover specified to extend 15' laterally in all directions from collection device
R309-515-7(7)(c) | At least one collection box provided for each collection area
R309-515-7(7)(d) | Access openings for junction and collection boxes meet requirements of R309-545
R309-515-7(7)(d) | Vents for junction and collection boxes meet requirements of R309-545
R309-515-7(7)(d) | Overflows for junction and collection boxes meet requirements of R309-545
R309-515-7(7)(d) | Adequate venting specified for junction and collection boxes
R309-515-7(7)(d) | Gaskets specified for lids for junction and collection boxes
N/A | Identify means of isolating or draining the junction and collection boxes for operation and maintenance
R309-515-7(7)(e) | Fencing at least 50' from collection devices specified around collection area on land equal to or higher in elevation
R309-515-7(7)(e) | Fencing at least 15' from collection devices specified around collection area on land lower in elevation
R309-515-7(7)(e) | Stock-tight fencing specified
R309-515-7(7)(e) | 6' high chain-linked fence with 3 strands of barbed wire specified in populated areas
R309-515-7(7)(f) | Specifications require removal of deep-rooted vegetation within fenced spring collection area
R309-515-7(7)(g) | Berm or channel immediately inside fenced collection area specified to divert all surface water runoff
R309-515-7(7)(h) | Permanent flow-measuring device, properly housed and protected, specified
R309-515-7(7)(i) | Spring fully developed to minimize excess water ponding within the spring collection area
R309-515-7(7)(i) | If ponding spring water is unavoidable, collect excess water by piping/French drain and route downgrade of collection area
Operation and Maintenance
R309-515-8(1)(a) | Periodically clear deep-rooted vegetation from collection area
R309-515-8(1)(a) | Frequently clear spring collection area and diversion channel
R309-515-8(1)(a) | Encourage growth of grasses and shallow-rooted vegetation
R309-515-8(1)(b) | Herbicides and pesticides may not be applied to spring collection area without Director's approval
R309-515-8(1)(b)(i-iii) | Herbicide and pesticide approval will only be granted for acceptable products without harmful substances
R309-515-8(2) | Oil-lubricated pumps shall use food grade mineral oil suitable for human consumption
R309-515-8(3) | Algicide shall not be applied without Director's approval and ANSI/NSF 60 certification