## Alternative SWT Checklist
Alternative Surface Water Treatment |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-530-4(1) | In addition to conventional surface water treatment (i.e. coagulation, sedimentation and filtration as outlined in R309-525), several alternative methods may also be suitable: Direct Filtration, Slow Sand Filtration, Membrane Filtration, and Diatomaceous Earth Filtration (informational)
R309-530-4(2) | Plans and specs for alternative treatment incorporate requirements from relevant sections of other drinking water engineering rules for the specified treatment method and where applicable include (a) through (j) below:
R309-530-4(2)(a) | Plant Siting (see R309-525-6)
R309-530-4(2)(b) | Pre-design Submittal (see R309-515-5(2))
R309-530-4(2)(c) | Plant Reliability (see R309-525-7)
R309-530-4(2)(d) | Color Coding and Pipe Marking (see R309-525-8)
R309-530-4(2)(e) | Chemical Addition (see R309-525-11)
R309-530-4(2)(f) | Miscellaneous Plant Facilities (see R309-525-17, particularly sub-section R309-525-17(1), Laboratory)
R309-530-4(2)(g) | Operation and Maintenance Manuals (see R309-525-19)
R309-530-4(2)(h) | Safety (see R309-525-21)
R309-530-4(2)(i) | Disposal of Treatment Plant Waste (see R309-525-23)
R309-530-4(2)(j) | Disinfection (see R309-520)
N/A | Project will resolve existing physical deficiencies
Direct Filtration - Chemical Addition and Mixing
R309-530-5(1) | Direct Filtration is conventional surface water treatment without the sedimentation process (informational)
R309-530-5(1) | Chemical Addition and Mixing for direct filtration meet requirements of sections R309-525-11 and R309-525-12
Direct Filtration - Source Water Quality
R309-530-5(2) | Direct Filtration applies destabilized colloids to the filter rather than removing the majority of the load through sedimentation (informational)
R309-530-5(2) | This process represents considerable construction cost savings, but the source water must have low average turbidity, generally only available from large-capacity reservoirs, in order to provide reliable service without excessive backwash requirements (informational)
Direct Filtration - Design Requirements
R309-530-5(3) | The direct filtration plant meets requirements (a) through (h) below:
R309-530-5(3)(a) | At least one year's record of source water turbidity, sampled at least once per week, has been submitted to the Director for review and acceptance
R309-530-5(3)(a) | A direct filtration facility will only be permitted if source water turbidity data show that 75% of the measurements are below five (5) NTU (informational)
R309-530-5(3)(b) | Pilot plant studies, acceptable to the Director, were conducted prior to the preparation of final engineering plans
R309-530-5(3)(c) | Requirements for flash mix and flocculation basin design meet sub-sections R309-525-12(1) and R309-525-12(2)
R309-530-5(3)(d) | Chemical addition & mixing equipment is designed to be able to provide a visible, but not necessarily settleable, floc
R309-530-5(3)(e) | Surface wash, subsurface wash, or air scour is provided for the filters in accordance with sub-section R309-525-15(7)
R309-530-5(3)(f) | A continuous monitoring turbidimeter is installed on each filter effluent line
R309-530-5(3)(f) | The continuous monitoring turbidimeter on each filter effluent line has at least two alarm conditions capable of meeting the requirements of R309-525-15(4)(b)(vi) or R309-525-15(4)(c)(vii)
R309-530-5(3)(f) | The combined plant effluent is equipped with a continuous turbidimeter having a chart recorder
R309-530-5(3)(f) | If required by DDW, additional monitoring equipment to assist in control of the coagulant dose has been provided (i.e. streaming current gauges, particle counters, etc.) when the plant can't consistently meet requirements of rule R309-200
R309-530-5(3)(g) | The plant is designed and operated so that the plant will automatically shut down when a source water turbidity of 20 NTU lasts longer than three hours or when the source water turbidity exceeds 30 NTU at any time
R309-530-5(3)(h) | The plant design and land ownership surrounding the plant allow for the installation of conventional sedimentation basins
R309-530-5(3)(h) | Sedimentation basins may be required if the Director determines the plant is failing to meet minimum water quality or performance standards (informational)
Slow Sand Filtration - Acceptability
R309-530-6(1) | Slow sand filtration is a process involving passage of raw water through a bed of sand at low velocity resulting in substantial particle removal by physical and biological mechanisms (informational)
R309-530-6(1) | Slow sand filters as a substitute for conventional surface water treatment facilities (detailed in R309-525) were determined to be acceptable by the Director based on suitability of the source water & system demand characteristics
Slow Sand Filtration - Source Water Quality
R309-530-6(2) | The Director has imposed design requirements additional to those listed below for use of slow sand filtration
R309-530-6(2) | Proposed slow sand filtration meets requirements (a) through (c) below:
R309-530-6(2)(a) | Source water turbidity is low and consistent
R309-530-6(2)(a) | The source water has a turbidity less than 50 NTU
R309-530-6(2)(a) | The source water has a color less than 30 units (see R309-515-5(2)(a))
R309-530-6(2)(b) | The nature of the turbidity particles has been considered
R309-530-6(2)(b) | Turbidity is not attributable to colloidal clay
R309-530-6(2)(c) | The nature and extent of algae growth in the raw water has been considered
R309-530-6(2)(c) | Any algae present is other than filter- and screen-clogging algae as indicated in "Standard Methods for the Examination of Water and Wastewater" (American Public Health Association, American Water Works Association, & Water Environment Federation)
R309-530-6(2)(c) | The amount of algae, expressed as the concentration of chlorophyll "a" in the raw water does not exceed 0.005 mg/l
Slow Sand Filtration - Pilot Plant Studies
R309-530-6(3) | The supplier's engineering studies show that the slow sand filter facility can consistently produce an effluent meeting the quality requirements of rule R309-200
R309-530-6(3) | The Director was consulted prior to the detailed design of a slow sand filter facility
Slow Sand Filtration - Operation
R309-530-6(4) | An active biological mat is created on the slow sand filter prior to introducing filtered water into the water system
Slow Sand Filtration - Design Requirements
R309-530-6(5) | The slow sand filtration plant meets requirements (a) through (l) below:
R309-530-6(5)(a) | At least three filter units are provided
R309-530-6(5)(a) | Where only three units are provided, any two are capable of meeting the plant's design capacity (normally the projected peak daily flow) at the approved filtration rate
R309-530-6(5)(a) | Where more than three filter units are provided, the filters are capable of meeting the plant design capacity at the approved filtration rate with any one filter removed from service
R309-530-6(5)(b) | All filters are protected to prevent freezing
R309-530-6(5)(b) | If covered by a structure, enough headroom exists to permit normal movement by operating personnel for scraping and sand removal operations
R309-530-6(5)(b) | There are adequate manholes and access ports for the handling of sand
R309-530-6(5)(b) | An overflow at the maximum filter water level is provided
R309-530-6(5)(c) | The permissible rates of filtration have been determined by the quality of the source water and by experimental data derived during pilot studies conducted on the source water
R309-530-6(5)(c) | Filtration rates of 0.03 gpm/sf to 0.1 gpm/sf are acceptable (equivalent to two to six million gallons per day per acre) (informational)
R309-530-6(5)(c) | Where higher filtration rates are proposed, they have been accepted by the Director
R309-530-6(5)(d) | Each filter unit is equipped with a main drain to collect filtered water
R309-530-6(5)(d) | Each filter unit is equipped with an adequate number of lateral underdrains to collect the filtered water
R309-530-6(5)(d) | The underdrains are spaced so that the maximum velocity of the water flow in the underdrain is ≤0.75 fps
R309-530-6(5)(d) | The maximum spacing of the underdrains is >3 feet when pipe laterals are used
R309-530-6(5)(e) | Filter sand is placed on graded gravel layers for an initial filter sand depth of 30 inches
R309-530-6(5)(e) | A minimum of 24 inches of filter sand is present, even after scraping
R309-530-6(5)(e) | The effective size of the filter sand is between 0.30 mm and 0.45 mm in diameter
R309-530-6(5)(e) | The filter sand uniformity coefficient is ≥2.5
R309-530-6(5)(e) | The sand is thoroughly washed, clean, and free from foreign matter
R309-530-6(5)(f) | A three-inch layer of well-rounded sand is used as a supporting media for filter sand
R309-530-6(5)(f) | The supporting media has an effective size of 0.8 mm to 2.0 mm in diameter
R309-530-6(5)(f) | The supporting media has a uniformity coefficient ≤1.7
R309-530-6(5)(g) | A supporting gravel media is provided
R309-530-6(5)(g) | The supporting gravel media consists of hard, durable, rounded silica particles
R309-530-6(5)(g) | Flat or elongated particles are absent from the supporting gravel media
R309-530-6(5)(g) | The coarsest gravel is 2.5 inches in size when the gravel rests directly on the strainer system and extends above the top of the perforated laterals
R309-530-6(5)(g) | A min. of four layers of gravel are provided in accordance with the following size and depth distribution when used with perforated laterals:
R309-530-6(5)(g) | Size: 2 ½ - 1 ½ in; Depth: 5 – 8 in
R309-530-6(5)(g) | Size: 1 ½ - ¾ in; Depth: 3 – 5 in
R309-530-6(5)(g) | Size: ¾ - ½ in; Depth: 3 – 5 in
R309-530-6(5)(g) | Size: ½ - 3/16 in; Depth: 2 – 3 in
R309-530-6(5)(g) | Size: 3/16 – 3/32 in; Depth: 2 – 3 in
R309-530-6(5)(g) | For proprietary filter bottoms with a reduced gravel depth, the Director has approved the reduced gravel depth
R309-530-6(5)(h) | Slow sand filters are designed to provide a depth of at least three to five feet of water over the sand
R309-530-6(5)(i) | Each filter is equipped with a loss of head gauge
R309-530-6(5)(i) | Each filter is equipped with an orifice
R309-530-6(5)(i) | Each filter is equipped with a venturi meter or other suitable metering device to control the rate of filtration
R309-530-6(5)(i) | Each filter is equipped with an effluent pipe designed to maintain the water level above the top of the filter sand
R309-530-6(5)(j) | Effluent from slow sand filtration plants is disinfected
R309-530-6(5)(k) | A provision for filter-to-waste is provided
R309-530-6(5)(l) | Electrical power is available at the plant site
Diatomaceous Earth Filtration
R309-530-7 | Diatomaceous Earth Filtration units may be considered for application to surface waters with low turbidity and low bacterial contamination (informational)
R309-530-7 | Diatomaceous Earth Filtration units may be used for iron removal for low quality groundwater, if the removal is effective and the water is of sanitary quality before treatment (informational)
R309-530-7 | The Director has accepted the use of Diatomaceous Earth Filtration as a substitute for "conventional surface water treatment" facilities (detailed in rule R309-525)
R309-530-7 | The Director has determined that the public water system management has previously exhibited an adequate level of support for the use of Diatomaceous Earth Filtration
R309-530-7 | The Director has found that conventional surface water treatment or other methods are too costly or unacceptable
R309-530-7 | Diatomaceous Earth Filtration consists of a process to remove particles from water by a precoat cake of diatomaceous earth filter media deposited on a support membrane (septum); water is filtered by passing through the cake on the septum, additional filter media known as body feed is continuously added to the source water to maintain the permeability of the filter cake (informational)
R309-530-7 | Diatomite filters are characterized by rigorous operating requirements, high operating costs, and increased sludge production (informational)
R309-530-7 | Design and operation of diatomaceous earth filtration facilities complies with Part 4, Section 4.2.3, Diatomaceous Earth Filtration, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Membrane Technology - Acceptability
R309-530-8(1) | Surface water or groundwater under the direct influence of surface water may be treated using membrane technology (microfiltration, ultrafiltration, nanofiltration) coupled with primary and secondary disinfection (informational)
Membrane Technology - Pilot Plant Study
R309-530-8(2) | The public water system has appropriately investigated the use of membrane technology to assure that the proposed process will produce the required quality of water at a cost which can be borne by the public water system consumers
R309-530-8(2) | A pilot plant study has been conducted prior to beginning design
R309-530-8(2) | The pilot plant study is conducted in accordance with EPA's Environmental Technology Verification Program (ETV) or the Director has approved the protocol and treated water parameters prior to conducting testing
Membrane Technology - Design Requirements
R309-530-8(3) | Items (a) and (b) below have been addressed in the design of a membrane technology plant intended to provide microbiological treatment of surface water or GWUDI water:
R309-530-8(3)(a) | The facility is equipped with an on-line particle counter on the final effluent
R309-530-8(3)(b) | The facility is equipped with an automatic membrane integrity test system
Membrane Technology - Turbidity Limits
R309-530-8(4) | The membrane treatment plant does not exceed the turbidity limit established by the Director for 95% of turbidity measurements
R309-530-8(4) | The membrane treatment plant does not exceed the maximum turbidity limit established by the Director
R309-530-8(4) | The membrane treatment plant effluent meets the requirements of R309-200-5(5)(a)(ii)
New Treatment Processes or Equipment
R309-530-9 | The policy of the Board is to encourage, rather than to obstruct, the development of new methods and equipment for the treatment of water (informational)
R309-530-9 | A New process or new equipment has been thoroughly tested in full-scale, comparable installations before plans have been submitted for review and approval (refer to EPA's Environmental Technology Verification Program (ETV))
R309-530-9 | The designer or supplier has presented evidence satisfactory to the Director that the new treatment process will insure the delivery of safe, sanitary water without imposing undue problems of supervision, operation, or control
R309-530-9 | The new treatment process does not exceed the turbidity limit established by the Director for 95% of turbidity measurements
R309-530-9 | The new treatment process does not exceed the maximum turbidity limit established by the Director
R309-530-9 | The new treatment process effluent meets the requirements of R309-200-5(5)(a)(ii)