## Conventional SWT Checklist
Conventional Surface Water Treatment |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-525-4(1) | Treatment plants for surface water or ground water under direct influence of surface water have facilities for coagulant chemical flash mixing, flocculation, sedimentation, filtration and disinfection
R309-525-4(2) | Overall design of treatment facility examined to assure compatibility of all devices and processes
R309-525-4(2) | Design of treatment processes and devices based on evaluation of nature and quality of particular water to be treated
R309-525-4(2) | Combined unit processes will produce water meeting all established drinking water standards per R309-200
R309-525-4(3) | Direct filtration, if proposed, follows R309-530-5 (optional)
R309-525-4(4) | Novel water treatment equipment or technique meets R309-530-9
N/A | Project will resolve existing physical deficiencies
Plant Capacity and Number of Treatment Trains
R309-525-5(1) | Required plant capacity and number of treatment trains determined after consultation with DDW
R309-525-5(1) | Minimum of two units each for flocculation, sedimentation, and filtration are provided
R309-525-5(1) | Design provides for parallel or series operation of the clarification stages
R309-525-5(1) | Flash mix is designed and operated to provide a minimum velocity gradient of 750 fps/ft
R309-525-5(1) | Mixing time is less than thirty seconds
R309-525-5(1) | If treatment plant is system’s sole source, it is designed to meet anticipated peak day demand of system being served
R309-525-5(1) | If other sources are available to the system, peak day demand treatment requirement is waived (optional)
R309-525-5(2) | DDW consulted for degree of back-up required at water treatment plant based on number of connections to be served, availability of other acceptable sources of water, and ability to control water consumption
R309-525-5(2) | Requirements of R309-525-7 (Plant Reliability) have been adjusted based on consultation with DDW (if multiple sources are available to the system)
Plant Siting
R309-525-6 | Treatment plant sited with regard to earthquakes
R309-525-6 | Treatment plant sited with regard to flooding
R309-525-6 | Treatment plant sited with regard to fire hazards
R309-525-6 | DDW was consulted regarding site selection prior to the preparation of engineering plans and specifications
Plant Reliability
R309-525-7 | Plant for treatment of surface water or GWUDI of surface water is designed to meet present and future water demands
R309-525-7 | Plant is designed to assure proper uninterrupted operation by meeting requirements (1) through (7) below:
R309-525-7(1) | Manual override is provided for all automatic controls
R309-525-7(1) | Adequate funding will be provided for maintenance of automatic equipment
R309-525-7(2) | Main switch electrical controls are located above grade
R309-525-7(2) | Main switch electrical controls are located in areas without flooding
R309-525-7(3) | Plant will be operated by qualified personnel approved by the Director
R309-525-7(3) | At minimum, treatment plant manager will be certified per R309-300 at the grade of the waterworks system with appropriate unrestricted Utah Operator's Certificate
R309-525-7(4) | Plant constructed to permit units to be taken out of service without disrupting operation
R309-525-7(4) | Plant constructed with drains or pumps sized to allow dewatering in a reasonable period of time
R309-525-7(5) | Plant has standby power available to permit operation of essential functions during power outages
R309-525-7(6) | Plant is provided with backup equipment or necessary spare parts for all critical items
R309-525-7(7) | Individual components critical to treatment plant operation are anchored to secure them from loss due to earthquake
Color Coding and Pipe Marking
R309-525-8 | Water treatment plant piping is color coded for identification
R309-525-8 | Identification of the direction of flow is indicated on pipes
R309-525-8 | Identification of contained liquid is indicated on pipes
Diversion Structures and Pretreatment
R309-525-9 | Diversion structure is designed per R309-515-5(5)
Pre-sedimentation
R309-525-10 | Water with heavy grit, sand, gravel, leaves, debris, or a large sediment volume has pretreatment, usually sedimentation, with or without the addition of coagulation chemicals
R309-525-10 | If provided, pretreatment meets requirements (1) through (3) below:
R309-525-10(1) | Presedimentation basins are equipped with efficient sludge removal
R309-525-10(2) | Incoming water will be dispersed across the full width of the line of travel as efficiently as practical
R309-525-10(2) | Short-circuiting is minimized
R309-525-10(3) | A bypass of the presedimentation process is provided
Chemical Addition - Standards
R309-525-11(1) | Surface water treatment chemicals meet requirements of (a) and (b) below:
R309-525-11(1)(a) | Primary coagulant chemicals are used to generate the formation of a floc
R309-525-11(1)(b) | Disinfectants are added to raw and/or treated water
Chemical Addition - Application Criteria
R309-525-11(2) | Chemicals applied to the water achieve requirements (a) through (d) below:
R309-525-11(2)(a) | Assure maximum control and flexibility of treatment
R309-525-11(2)(b) | Assure maximum safety to consumer and operators
R309-525-11(2)(c) | Prevent backflow or back-siphonage of chemical solutions to finished water systems
R309-525-11(2)(d) | Chemical feed spaced to eliminate any interference between chemicals
Chemical Addition - Typical Chemical Doses
R309-525-11(3) | Chemical doses are estimated for each treatment plant to be designed
R309-525-11(3) | Jar tests have been conducted on representative raw water samples to determine anticipated doses
Chemical Addition - Information Required for Review
R309-525-11(4) | Items (a) through (g) below for chemical application have been submitted and approved by the Director:
R309-525-11(4)(a) | Description of feed equipment, including maximum and minimum feed rates
R309-525-11(4)(b) | Location of feeders, piping layout and points of application
R309-525-11(4)(c) | Chemical storage and handling facilities
R309-525-11(4)(d) | Specifications for chemicals to be used
R309-525-11(4)(e) | Operating and control procedures including proposed application rates
R309-525-11(4)(f) | Descriptions of testing equipment and procedures
R309-525-11(4)(g) | Results of chemical, physical, biological and other tests performed as needed to define optimum chemical treatment
Chemical Addition - Quality of Chemicals
R309-525-11(5) | All chemicals added to water being treated for use in a public water system for human consumption meet ANSI/NSF 60
R309-525-11(5) | The chemical shipping container labels or material safety data sheets include items (a) and (b) below:
R309-525-11(5)(a) | Chemical name, purity and concentrations, supplier name and address
R309-525-11(5)(b) | Labeling indicating compliance with ANSI/NSF 60
Chemical Addition - Chemical Storage, Safe Handling and Ventilation
R309-525-11(6) | Utah Occupational Safety & Health Act (UOSHA) requirements for chemical storage, safe handling & ventilation are met
R309-525-11(6) | The design incorporates all applicable UOSHA standards
R309-525-11(6) | DDW review of facility plans under this rule will be limited to requirements (a) and (b) below:
Chemical Addition - Chemical Storage, Safe Handling and Ventilation - (a) Chemical Storage
R309-525-11(6)(a) | Chemical Storage meets requirements (i) through (v) below:
R309-525-11(6)(a)(i) | Space is provided for (A) through (C) below:
R309-525-11(6)(a)(i)(A) | An adequate supply of chemicals
R309-525-11(6)(a)(i)(B) | Convenient and efficient handling of chemicals
R309-525-11(6)(a)(i)(C) | Dry storage conditions
R309-525-11(6)(a)(ii) | Storage tanks and pipelines for liquid chemicals are specific to the chemicals and not for alternatives
R309-525-11(6)(a)(iii) | Chemicals are stored in covered/unopened shipping containers, unless chemical is transferred to a covered storage unit
R309-525-11(6)(a)(iv) | Liquid chemical storage tanks meet requirements (A) through (C) below:
R309-525-11(6)(a)(iv)(A) | Tanks have a liquid level indicator
R309-525-11(6)(a)(iv)(B) | Tanks have an overflow & receiving basin/drain, meeting requirements of R309-525-23, able to receive spills/overflows
R309-525-11(6)(a)(iv)(C) | Tanks are equipped with an inverted "J" air vent
R309-525-11(6)(a)(v) | Acids are kept in closed, acid-resistant shipping containers or storage units
Chemical Addition - Chemical Storage, Safe Handling and Ventilation - (b) Safe Handling
R309-525-11(6)(b)(i) | Material Safety Data Sheets for all chemicals kept and maintained in prominent display easily accessible by operators
R309-525-11(6)(b)(ii) | Acceptable procedure followed for disposing of empty bags, drums or barrels that minimizes operator exposure to dust
R309-525-11(6)(b)(iii) | Provision is made for measuring quantities of chemicals used to prepare feed solutions
Chemical Addition - Chemical Storage, Safe Handling and Ventilation - (c) Dust Control and Ventilation
R309-525-11(6)(c) | Adequate provision is made for dust control and ventilation
Chemical Addition - Feeder Design, Location, and Control - General Feeder Design
R309-525-11(7)(a) | General equipment design, location, and control meets requirements (i) through (x) below:
R309-525-11(7)(a)(i) | Feeders supply necessary amounts of chemicals at accurately controlled rate, throughout anticipated feed range
R309-525-11(7)(a)(ii) | Chemical-contact materials and surfaces are resistant to the aggressiveness of the chemicals
R309-525-11(7)(a)(iii) | Corrosive chemicals are introduced in a manner to minimize potential for corrosion
R309-525-11(7)(a)(iv) | Incompatible chemicals are not fed, stored, or handled together
R309-525-11(7)(a)(v) | All chemicals are conducted from the feeder to the point of application in separate conduits
R309-525-11(7)(a)(vi) | Spare parts are available for all feeders to replace parts subject to wear and damage
R309-525-11(7)(a)(vii) | Chemical feeders are as near as practical to the feed point
R309-525-11(7)(a)(viii) | Chemical feeders and pumps operate at no lower than 20 percent of the feed range
R309-525-11(7)(a)(ix) | Chemicals are fed by gravity where practical
R309-525-11(7)(a)(x) | Equipment is readily accessible for servicing, repair, and observation
Chemical Addition - Feeder Design, Location, and Control - Chemical Feed Equipment
R309-525-11(7)(b) | Where chemical feed, such as disinfection, is necessary for the protection of the consumer, coagulation or other essential processes meet requirements (i) through (v) below:
R309-525-11(7)(b)(i) | A minimum of two feeders, one active and one standby, are provided for each chemical
R309-525-11(7)(b)(ii) | A standby unit or a combination of units of sufficient capacity is available to replace the largest unit during shut-downs
R309-525-11(7)(b)(iii) | Where a booster pump is required, duplicate equipment is provided and, when necessary, standby power
R309-525-11(7)(b)(iii) | Where a booster pump is required, standby power is provided, when necessary
R309-525-11(7)(b)(iv) | A separate feeder is used for each non-compatible chemical applied where a feed pump is required
R309-525-11(7)(b)(v) | Spare parts are available for all feeders to replace parts that are subject to wear and damage
Chemical Addition - Feeder Design, Location, and Control - Dry Chemical Feeders
R309-525-11(7)(c) | Dry chemical feeders meet the requirements (i) and (ii) below:
R309-525-11(7)(c)(i) | Feed rate of chemicals is measured volumetrically or gravimetrically
R309-525-11(7)(c)(ii) | Adequate solution water and agitation of the chemical in the solution tank is provided
Chemical Addition - Feeder Design, Location, and Control - Feed Rate Control
R309-525-11(7)(d)(i) | Feeders can be manually or automatically controlled (optional)
R309-525-11(7)(d)(i) | Automatic controls are designed to allow override by manual controls
R309-525-11(7)(d)(ii) | Chemical feed rates are proportional to flows
R309-525-11(7)(d)(iii) | A means to measure water flow is provided
R309-525-11(7)(d)(iv) | Provision made for measuring the quantities of chemicals used
R309-525-11(7)(d)(v)(A) | Scales are provided for weighing cylinders at all plants using chlorine gas
R309-525-11(7)(d)(v)(B) | Scales are provided, if applicable, for fluoride solution feed
R309-525-11(7)(d)(v)(C) | Scales are provided for volumetric dry chemical feeders
R309-525-11(7)(d)(v)(D) | Scales are accurate to measure increments of 0.5 percent of scale capacity
Chemical Addition - Feeder Appurtenances - Liquid Chemical Solution Pumps
R309-525-11(8)(a) | Positive displacement type solution feed pumps are used to feed liquid chemicals
R309-525-11(8)(a) | Positive displacement type solution feed pumps are absent when feeding chemical slurries
R309-525-11(8)(a) | Pumps are sized to match or exceed maximum head conditions found at the point of injection
R309-525-11(8)(a) | All liquid chemical feeders have devices approved by Utah Plumbing Code to prevent chemical siphoning through pump
Chemical Addition - Feeder Appurtenances - Solution Tanks
R309-525-11(8)(b)(i) | Means consistent with nature of chemical solution is provided in solution tank to maintain uniform solution strength
R309-525-11(8)(b)(i) | Continuous agitation is provided to maintain slurries in suspension
R309-525-11(8)(b)(ii) | Means provided to measure the solution level in the tank
R309-525-11(8)(b)(iii) | Chemical solutions are kept covered
R309-525-11(8)(b)(iii) | Access openings on large tanks are curbed and fitted with tight overhanging covers
R309-525-11(8)(b)(iv) | Subsurface locations are discouraged (recommendation)
R309-525-11(8)(b)(iv) | If present, a subsurface location for solution tanks meet the requirements (A) and (B) below:
R309-525-11(8)(b)(iv)(A) | Are free from sources of possible contamination
R309-525-11(8)(b)(iv)(B) | Assure positive drainage for ground water, accumulated water, chemical spills, and overflows
R309-525-11(8)(b)(v) | Overflow pipes meet requirements (A) and (B) below:
R309-525-11(8)(b)(v)(A) | Have a free fall discharge
R309-525-11(8)(b)(v)(B) | Are located where noticeable
R309-525-11(8)(b)(vi) | Acid storage tanks are vented to the outside atmosphere (not through vents in common with day tanks)
R309-525-11(8)(b)(vii) | Each tank is provided with a valved drain, protected against backflow per R309-525-11(10)(b) and R309-525-11(10)(c)
R309-525-11(8)(b)(viii) | Solution tanks are located to prevent chemicals from equipment failure, spills, or accidental drainage from entering water in conduits, treatment, or storage basins
R309-525-11(8)(b)(viii) | Solution tanks have protective curbing provided to prevent chemicals from equipment failure, spills, or accidental drainage from entering the water in conduits, treatment, or storage basins
R309-525-11(8)(b)(ix) | When polymers are used, storage tanks are located away from heat sources
R309-525-11(8)(b)(ix) | When polymers are used, storage tanks are located away from direct sunlight
Chemical Addition - Feeder Appurtenances - Day Tanks
R309-525-11(8)(c)(i) | Day tanks are provided where dilution of liquid chemical is required prior to feeding
R309-525-11(8)(c)(ii) | Day tanks meet all requirements of R309-525-11(9)(b)
R309-525-11(8)(c)(iii) | Day tanks hold no more than a thirty hour supply (unless manufacturer's recommendations allow for longer periods) for chemicals, such as polymers, that become unstable after hydration
R309-525-11(8)(c)(iv) | Day tanks are scale-mounted, have a calibrated gauge painted or mounted on the side if liquid levels cannot be seen in a gauge tube or through translucent tank sidewalls, or have a gauge rod extending above a referenced point at the top of the tank attached to a float in opaque tanks
R309-525-11(8)(c)(iv) | The ratio of the cross-sectional area of the tank to its height is such that unit readings are meaningful in relation to the total amount of chemical fed during a day
R309-525-11(8)(c)(v) | Hand pumps are provided for transfer from a carboy or drum (optional)
R309-525-11(8)(c)(v) | A top rack is used to permit withdrawal into a bucket from a spigot (optional)
R309-525-11(8)(c)(v) | With motor-driven transfer pumps, a liquid level limit switch and an overflow from the day tank, which will drain by gravity back into the bulk storage tank, is provided, unless spill containment is provided for both bulk and day tanks
R309-525-11(8)(c)(vi) | Means consistent with the nature of the chemical solution provided to maintain uniform solution strength in a day tank
R309-525-11(8)(c)(vi) | Continuous agitation is provided to maintain chemical slurries in suspension
R309-525-11(8)(c)(vii) | Tanks are properly labeled to designate the chemical inside
Chemical Addition - Feeder Appurtenances - Feed Lines
R309-525-11(8)(d)(i) | Feed line length of run is as short as possible
R309-525-11(8)(d)(i) | Feed lines meet requirements (A) through (D) below:
R309-525-11(8)(d)(i)(A) | Are made of durable, corrosion resistant material
R309-525-11(8)(d)(i)(B) | Are easily accessible throughout the entire length
R309-525-11(8)(d)(i)(C) | Are protected against freezing
R309-525-11(8)(d)(i)(D) | Are readily cleanable
R309-525-11(8)(d)(ii) | Feed lines slope upward from the chemical source to the feeder when conveying gases
R309-525-11(8)(d)(iii) | Feed lines are designed to consider scale forming or solids depositing properties of the water, chemical, solution, or mixture conveyed
Chemical Addition - Make-up Water Supply and Protection - In-Plant Water Supply
R309-525-11(9)(a) | In-plant water supply meets requirements (i) through (iii) below:
R309-525-11(9)(a)(i) | Supply is ample
R309-525-11(9)(a)(i) | Pressure is adequate
R309-525-11(9)(a)(i) | Quality is equal to or better than the water at the point of application
R309-525-11(9)(a)(ii) | Provided with means for measurement when preparing specific solution concentrations by dilution
R309-525-11(9)(a)(iii) | Properly protected against backflow
Chemical Addition - Make-up Water Supply and Protection - Cross-Connection Control
R309-525-11(9)(b) | Cross-connection control meets requirements (i) through (iv) below:
R309-525-11(9)(b)(i) | Make-up waterlines discharging to solution tanks are properly protected from backflow per the Utah Plumbing Code
R309-525-11(9)(b)(ii) | Liquid chemical solutions can't be siphoned through solution feeders into process units by meeting R309-525-11(9)(c)
R309-525-11(9)(b)(iii) | No direct connection exists between any sewer and the drain or overflow from the feeder, solution chamber, or tank by providing that all pipes terminate at least six inches or two pipe diameters, whichever is greater, above the overflow rim of a receiving sump, conduit, or waste receptacle
R309-525-11(9)(b)(iv) | Pre- and post-chlorination systems are independent to prevent siphoning of partially treated water into the clear well
R309-525-11(9)(b)(iv) | The water supply to each eductor has a separate shut-off valve
R309-525-11(9)(b)(iv) | A master shut off valve is absent
Chemical Addition - Make-up Water Supply and Protection - Liquid Chemical Feeders, Siphon Control
R309-525-11(9)(c) | Liquid chemical feeders meet (i) through (iv) below (chemical solutions can't be siphoned into process units):
R309-525-11(9)(c)(i) | Positive pressure is assured at the point of discharge
R309-525-11(9)(c)(ii) | Vacuum relief is provided
R309-525-11(9)(c)(iii) | A suitable air gap is provided
R309-525-11(9)(c)(iv) | Other suitable means or combinations are provided as necessary
Chemical Addition - Operator Safety
R309-525-11(10) | A treatment plant is designed and operated per UOSHA and includes (a) through (d) below:
R309-525-11(10)(a) | Floor surfaces are smooth
R309-525-11(10)(a) | Floor surfaces are impervious
R309-525-11(10)(a) | Floor surfaces are slip-proof
R309-525-11(10)(a) | Floor surfaces are well drained
R309-525-11(10)(b) | At least one pair of rubber gloves is provided for each operator
R309-525-11(10)(b) | A dust respirator certified by NIOSH for toxic dusts is provided for each operator
R309-525-11(10)(b) | An apron or other protective clothing is provided for each operator
R309-525-11(10)(b) | Goggles or a face mask is provided for each operator
R309-525-11(10)(b) | A deluge shower is provided where strong acids or alkalis are used or stored
R309-525-11(10)(b) | An eye wash is provided where strong acids or alkalis are used or stored
R309-525-11(10)(c) | A water holding tank that will allow water to reach room temperature, or other tempering method, should be installed in the water line feeding the deluge shower (recommendation)
R309-525-11(10)(c) | A water holding tank that will allow water to reach room temperature, or other tempering methods, should be installed in the water line feeding the eye wash (recommendation)
R309-525-11(10)(d) | Adequate ventilation should be provided (recommendation)
Chemical Addition - Design for Specific Chemicals
R309-525-11(11) | A treatment plant is designed and operated according to Utah Occupational Safety and Health Act (UOSHA) and meets the requirements for the appropriate chemical category below:
R309-525-11(11) | Acids and Caustics:
R309-525-11(11) | (i) Acids and caustics are kept in closed, corrosion-resistant shipping containers or storage units
R309-525-11(11) | (ii) Acids and caustics are handled in closed vessels and are pumped in undiluted form from original containers through a suitable hose to the point of treatment or to a covered day tank
R309-525-11(11) | Sodium Chlorite for Chlorine Dioxide Generation:
R309-525-11(11) | Proposal for storage & use of sodium chlorite has been approved by the Director prior to preparing final plans & specs
R309-525-11(11) | Provisions are made for proper storage and handling of sodium chlorite to eliminate any danger of explosion
R309-525-11(11) | (i) Sodium Chlorite Storage meets (A) through (C):
R309-525-11(11) | (A) Sodium chlorite is stored alone in a separate room in an outside building detached from water treatment facility
R309-525-11(11) | (A) Sodium chlorite is stored away from organic materials that would react violently with it
R309-525-11(11) | (B) Storage structures are constructed of noncombustible materials
R309-525-11(11) | (C) If the storage structure is to be located in a area where a fire may occur, water is available to keep the sodium chlorite area sufficiently cool to prevent decomposition from heat and resultant potential explosive conditions
R309-525-11(11) | ii) Sodium Chlorite Handling meets (A) through (C):
R309-525-11(11) | (A) Care is taken to prevent spillage (recommendation)
R309-525-11(11) | (B) An emergency plan of operation is available for the clean-up of any spillage
R309-525-11(11) | (C) Storage drums are thoroughly flushed prior to recycling or disposal (recommendation)
R309-525-11(11) | (iii) Sodium Chlorite Feeders meet (A) through (D):
R309-525-11(11) | (A) Positive displacement feeders are provided (recommendation)
R309-525-11(11) | (B) Tubing for conveying sodium chlorite or chlorine dioxide solutions is Type 1 PVC, polyethylene, or materials recommended by the manufacturer
R309-525-11(11) | (C) Feed lines are installed in a manner to prevent formation of gas pockets Feed lines terminate at a point of positive pressure
R309-525-11(11) | (C) Feed lines terminate at a point of positive pressure
R309-525-11(11) | (D) Check valves are provided to prevent the backflow of chlorine into the sodium chlorite line
Mixing - Flash Mix - Equipment
R309-525-12(1)(a) | Mechanical, in-line or jet mixing devices are used
Mixing - Flash Mix - Mixing
R309-525-12(1)(b) | All devices used in rapid mixing are capable of imparting a minimum velocity gradient (G) of at least 750 fps per foot
R309-525-12(1)(b) | Mixing time is less than thirty seconds
Mixing - Flash Mix - Location
R309-525-12(1)(c) | The flash mix and flocculation basins are as close together as possible
Mixing - Flash Mix - Introduction of Chemicals
R309-525-12(1)(d) | Primary coagulant chemicals are added at the point of maximum turbulence within the flash mix unit
R309-525-12(1)(d) | Where in-line mixing devices are used chemical injection is at the most appropriate upstream point
Mixing - Flocculation - Basin Design
R309-525-12(2)(a) | Inlet and outlet design prevents short-circuiting and destruction of floc
R309-525-12(2)(a) | A drain or pump is provided to handle dewatering and sludge removal
Mixing - Flocculation - Detention
R309-525-12(2)(b) | Flow-through velocity is ≥0.5 feet per minute and ≤1.5 feet per minute with a detention time for floc formation of at least 30 minutes
Mixing - Flocculation - Equipment
R309-525-12(2)(c) | Agitators are driven by variable speed drives with the peripheral speed of paddles ranging from 0.5 fps to 2.0 fps
R309-525-12(2)(c) | Equipment is capable of imparting a velocity gradient (G) between 25 fps per foot & 80 fps per foot to the water treated
R309-525-12(2)(c) | Compartmentalized tapered energy flocculation concept may be used where G tapers from 100 to 10 fps per ft (optional)
Mixing - Flocculation - Hydraulic Flocculation
R309-525-12(2)(d) | Hydraulic flocculation may be permitted on a case-by-case basis (the unit must yield a G value equivalent to that required by R309-525-12(2)(b) and (c) above) (optional)
Mixing - Flocculation - Piping
R309-525-12(2)(e) | Flocculation and sedimentation basins are as close as possible
R309-525-12(2)(e) | The velocity of flocculated water through pipes or conduits to settling basins is ≥0.5 feet per second and ≤1.5 fps
R309-525-12(2)(e) | Turbulence is minimized at bends and changes in direction
Mixing - Flocculation - Other Designs
R309-525-12(2)(f) | Baffling is used to provide for flocculation in small plants if approved by the Director (design maintains the velocities and flows noted above)
Mixing - Flocculation - Visible Floc
R309-525-12(2)(g) | The flocculation unit is capable of producing a visible, settleable floc
Sedimentation - General Design Requirements
R309-525-13(1) | Sedimentation follows flocculation
R309-525-13(1) | The detention time for effective clarification is dependent upon a number of factors related to basin design and the nature of the raw water (informational)
R309-525-13(1) | Conventional sedimentation units meet requirements (a) through (h) below:
Sedimentation - General Design Requirements - (a) Inlet Devices
R309-525-13(1)(a) | Inlets are designed to distribute the water equally and at uniform velocities
R309-525-13(1)(a) | Open ports, submerged ports, or similar entrance arrangements are provided
R309-525-13(1)(a) | A baffle is constructed across the basin, close to the inlet end, and projects several feet below the water surface to dissipate inlet velocities and provide uniform flows across the basin
Sedimentation - General Design Requirements - (b) Outlet Devices
R309-525-13(1)(b) | Outlet devices are designed to maintain velocities suitable for settling in the basin and to minimize short-circuiting
R309-525-13(1)(b) | The use of submerged orifices is recommended to provide a volume above the orifices for storage when there are fluctuations in the flow (recommendation)
Sedimentation - General Design Requirements - (c) Emergency Overflow
R309-525-13(1)(c) | An overflow weir (or pipe) is installed to establish the maximum water level desired on top of the filters
R309-525-13(1)(c) | Overflow weir (or pipe) discharges by gravity with a free fall to a location where the discharge will be visible
Sedimentation - General Design Requirements - (d) Sludge Removal
R309-525-13(1)(d) | Sludge removal design meets (i) through (v) below:
R309-525-13(1)(d)(i) | Sludge pipes are min. three inches in diameter
R309-525-13(1)(d)(i) | Sludge pipes are arranged to facilitate cleaning
R309-525-13(1)(d)(ii) | Entrance to sludge withdrawal piping prevents clogging
R309-525-13(1)(d)(iii) | Valves are located outside the basin for accessibility
R309-525-13(1)(d)(iv) | The operator may observe and sample sludge being withdrawn from the unit
R309-525-13(1)(d)(v) | Sludge collection is done by mechanical means
Sedimentation - General Design Requirements - (e) Drainage
R309-525-13(1)(e) | Basins are provided with a means for dewatering
R309-525-13(1)(e) | Basin bottoms slope toward the drain not less than one foot in 12 feet where mechanical sludge collection equipment is not provided
Sedimentation - General Design Requirements - (f) Flushing Lines
R309-525-13(1)(f) | Flushing lines or hydrants are provided
R309-525-13(1)(f) | Flushing lines or hydrants are equipped with backflow prevention devices acceptable to the Director
Sedimentation - General Design Requirements - (g) Safety
R309-525-13(1)(g) | Appropriate safety devices are included as required by the Occupational Safety and Health Act (OSHA)
Sedimentation - General Design Requirements - (h) Removal of Floating Material
R309-525-13(1)(h) | Provisions are made for the periodic removal of floating material
Sedimentation - Sedimentation Without Tube Settlers
R309-525-13(2) | If tube settling equipment is not used within settling basins, requirements (a) through (d) below are met:
Sedimentation - Sedimentation Without Tube Settlers - (a) Detention Time
R309-525-13(2)(a) | A minimum of four hours of detention time is provided
R309-525-13(2)(a) | Reduced sedimentation time has been approved because equivalent effective settling has been demonstrated or multimedia filtration is employed
Sedimentation - Sedimentation Without Tube Settlers - (b) Weir Loading
R309-525-13(2)(b) | The rate of flow over the outlet weir is ≤20,000 gallons per day per foot of weir length
R309-525-13(2)(b) | Where submerged orifices are used as an alternate for overflow weirs, they are max. of three feet below the water surface when the flow rates are equivalent to weir loading
Sedimentation - Sedimentation Without Tube Settlers - (c) Velocity
R309-525-13(2)(c) | The velocity through settling basins is max. of 0.5 feet per minute
R309-525-13(2)(c) | The basins are designed to minimize short-circuiting
R309-525-13(2)(c) | Fixed or adjustable baffles are provided as necessary to achieve the maximum potential for clarification
Sedimentation - Sedimentation Without Tube Settlers - (d) Depth
R309-525-13(2)(d) | The depth of the sedimentation basin is designed for optimum removal
Sedimentation - Sedimentation With Tube Settlers
R309-525-13(3) | Proposal for settler unit clarification has been approved by the Director prior to the preparation of final plans and specs
R309-525-13(3)(a) | Inlet and outlet design maintains velocities suitable for settling in the basin
R309-525-13(3)(a) | Inlet and outlet design minimizes short circuiting
R309-525-13(3)(b) | Flushing lines are provided to facilitate maintenance
R309-525-13(3)(b) | Flushing lines are properly protected against backflow or back siphonage
R309-525-13(3)(b) | Drain and sludge piping from the settler units are sized to facilitate a quick flush of the settler units
R309-525-13(3)(b) | Drain and sludge piping from settler units are sized to prevent flooding other portions of the plant
R309-525-13(3)(c) | For outdoor installations, design provides sufficient freeboard above the top of settlers to prevent units from freezing
R309-525-13(3)(d) | The design application rate is a max. of 2 gal/sq.ft./min of cross-sectional area (based on 24-inch long 60 degree tubes or 39.5-inch long 7.5 degree tubes), unless higher rates are successfully shown through pilot plant or in-plant demonstration studies
Solids Contact Units - General
R309-525-14(1) | Solids contact units are generally acceptable for combined softening and clarification where water characteristics, especially temperature, do not fluctuate rapidly, flow rates are uniform, and operation is continuous (informational)
R309-525-14(1) | Before solids contact units are considered as clarifiers without softening, approval of Director has been obtained
R309-525-14(1) | A minimum of two units are provided for surface water treatment
Solids Contact Units - Installation of Equipment
R309-525-14(2) | Representative of the manufacturer is present at the time of initial start-up operation to assure that the units are operating properly
Solids Contact Units - Operation of Equipment
R309-525-14(3) | Items (a) through (c) below are provided for plant operation:
R309-525-14(3)(a) | A complete outfit of tools and accessories
R309-525-14(3)(b) | Necessary laboratory equipment
R309-525-14(3)(c) | Adequate piping with suitable sampling taps located to permit the collection of water samples from critical portions of the units
Solids Contact Units - Chemical Feed
R309-525-14(4) | Chemicals are applied at such points and by such means as to insure satisfactory mixing of the chemicals with the water
Solids Contact Units - Mixing
R309-525-14(5) | A flash mix device or chamber ahead of solids contact units may be required to assure proper mixing of the chemicals applied (informational)
R309-525-14(5) | Mixing devices employed are constructed to provide (a) and (b) below:
R309-525-14(5)(a) | Provide good mixing of the raw water with previously formed sludge particles
R309-525-14(5)(b) | Prevent deposition of solids in the mixing zone
Solids Contact Units - Flocculation
R309-525-14(6) | Flocculation equipment meets requirements (a) through (c) below:
R309-525-14(6)(a) | Speed and/or pitch are adjustable
R309-525-14(6)(b) | Coagulation in a separate chamber or baffled zone within the unit is provided
R309-525-14(6)(c) | Flocculation and mixing period is not less than 30 minutes
Solids Contact Units - Sludge Concentrators
R309-525-14(7)(a) | Equipment provides either internal or external concentrators to obtain concentrated sludge with a min. of waste water
R309-525-14(7)(b) | Large basins have at least two sumps for collecting sludge with one sump located in the central flocculation zone
Solids Contact Units - Sludge Removal
R309-525-14(8) | Sludge removal design meets requirements (a) through (d) below:
R309-525-14(8)(a) | Sludge pipes are min. of three inches in diameter
R309-525-14(8)(a) | Sludge pipes are arranged to facilitate cleaning
R309-525-14(8)(b) | The entrance to the sludge withdrawal piping prevents clogging
R309-525-14(8)(c) | Valves are located outside the tank for accessibility
R309-525-14(8)(d) | The operator may observe and sample sludge being withdrawn from the unit
Solids Contact Units - Cross Connections
R309-525-14(9)(a) | Blow-off outlets and drains terminate and discharge at places satisfactory to the Director
R309-525-14(9)(b) | Cross-connection control is included for the finished drinking water lines used to back flush the sludge lines
Solids Contact Units - Detention Period
R309-525-14(10) | Detention time is established on the basis of raw water characteristics & other local conditions that affect unit operation
R309-525-14(10) | Based on design flow rates, the detention time meets either (a) or (b) below:
R309-525-14(10)(a) | Two to four hours for suspended solids contact clarifiers and softeners treating surface water
R309-525-14(10)(b) | One to two hours for suspended solids contact softeners treating only ground water
Solids Contact Units - Suspended Slurry Concentrate
R309-525-14(11) | Softening units are designed so continuous slurry concentrates of ≥1%, by weight, can be satisfactorily maintained
Solids Contact Units - Water Losses
R309-525-14(12)(a) | Units are provided with suitable controls for sludge withdrawal
R309-525-14(12)(b)(i) | Total water losses are a max. of five percent for clarifiers
R309-525-14(12)(b)(ii) | Total water losses are a max. of three percent for softening units
Solids Contact Units - Weirs or Orifices
R309-525-14(13) | The units are equipped with either overflow weirs or orifices constructed so that water at the surface of the unit travels ≤10 feet horizontally to the collection trough
R309-525-14(13)(a) | Weirs are adjustable, and at least equivalent in length to the perimeter of the basin
R309-525-14(13)(b)(i) | Weir loading is a max. of 10 gpm per foot of weir length for units used for clarifiers
R309-525-14(13)(b)(ii) | Weir loading is a max. of 20 gpm per foot of weir length for units used for softeners
R309-525-14(13)(c) | Where orifices are used, the loading rates per foot of launderer are equivalent to weir loadings
R309-525-14(13)(c) | Either orifices or weirs produce uniform rising rates over the entire area of the tank
Solids Contact Units - Upflow Rates for Clarifiers
R309-525-14(14)(a) | Upflow rate max. of 1.0 gpm/sf at the sludge separation line for units used for clarifiers
Solids Contact Units - Upflow Rates for Softeners
R309-525-14(14)(b) | Upflow rate max. of 1.75 gpm/sf at the slurry separation line for units used as softeners
Filtration - General
R309-525-15(1) | Filters may be composed of one or more media layers (informational)
R309-525-15(1) | Mono-media filters are relatively uniform throughout their depth (informational)
R309-525-15(1) | Dual or multi-layer beds of filter material are designed so that water being filtered first encounters coarse material and progressively finer material as it travels through the bed (informational)
Filtration - Rate of Filtration
R309-525-15(2)(a) | The rate of filtration is based on such factors as raw water quality, degree of pretreatment provided, filter media, water quality control parameters, competency of operating personnel, and other factors as determined by the Director
R309-525-15(2)(a) | Generally, higher filter rates can be assigned for the dual or multi-media filter than for a single media filter because the former is more resistant to filter breakthrough (informational)
R309-525-15(2)(b) | Filter rate is proposed and justified to the satisfaction of the Director prior to the preparation of final plans and specs
R309-525-15(2)(c) | Sedimentation detention time (see R309-525-13(2)(a)) is reduced with the use of dual or multi-media filters due to their increased ability to store sludge
R309-525-15(2)(d) | Filter rates assigned by the Director will never be exceeded, even during backwash periods
R309-525-15(2)(e) | The use of filter types other than conventional rapid sand gravity filters have received written approval from the Director prior to the preparation of final plans and specifications
Filtration - Number of Filters Required
R309-525-15(3) | At least two filter units are provided
R309-525-15(3) | Where only two filter units are provided, each is capable of meeting the plant design capacity (normally the projected peak day demand) at the approved filtration rate
R309-525-15(3) | Where more than two filter units are provided, filters are capable of meeting the plant design capacity at the approved filtration rate with one filter removed from service
Filtration - Media Design
R309-525-15(4) | At a min., filter media are designed to meet appropriate requirements of (a) through (e) below:
R309-525-15(4) | Media meets more stringent design requirements required by Director
Filtration - Media Design - (a) Mono-Media, Rapid Rate Gravity Filters
R309-525-15(4)(a) | The allowable maximum filtration rate for a silica sand, mono-media filter is three gpm/sf
R309-525-15(4)(a) | Filter is composed of clean silica sand having an effective size of 0.35 mm to 0.65 mm and having a uniformity coefficient less than 1.7
R309-525-15(4)(a) | The total bed thickness is min. of 24 inches and max. of 30 inches
Filtration - Media Design - (b) Dual Media, Rapid Rate Gravity Filters
R309-525-15(4)(b) | Dual media filters meet requirements (i) through (vi) below:
R309-525-15(4)(b)(i) | Total depth of filter bed is min. of 24 inches and max. of 30 inches
R309-525-15(4)(b)(ii) | All materials used to make up the filter bed are of such particle size and density that they will be effectively washed at backwash rates between 15 and 20 gpm/sf
R309-525-15(4)(b)(ii) | Materials will settle to reconstitute the bed in the original layers upon completion of backwashing
R309-525-15(4)(b)(iii) | The bottom layer is min. of ten inches thick and consists of a material having an effective size ≤0.45 mm and a uniformity coefficient ≤1.5
R309-525-15(4)(b)(iv) | Top layer is clean crushed anthracite coal with an effective size of 0.45 mm to 1.2 mm and a uniformity coefficient ≤1.5
R309-525-15(4)(b)(v) | Dual media filters will be assigned a filter rate up to six gpm/sf
R309-525-15(4)(b)(v) | Generally if the bottom fine layer consists of a material having an effective size of 0.35 mm or less, a filtration rate of six gpm/sf can be assigned (informational)
R309-525-15(4)(b)(vi) | Each dual media filter is provided with equipment that continuously monitors turbidity in the filtered water
R309-525-15(4)(b)(vi) | The equipment is designed to initiate automatic backwash if the filter effluent turbidity exceeds 0.3 NTU
R309-525-15(4)(b)(vi) | If the filter turbidity exceeds one NTU, the filter will be shut down
R309-525-15(4)(b)(vi) | In plants attended part-time, filter shutdown is accomplished automatically and accompanied by an alarm
R309-525-15(4)(b)(vi) | In plants with full-time operators, a one NTU condition activates an alarm
R309-525-15(4)(b)(vi) | In plants with full-time operators, when a one NTU condition occurs, filter shutdown may then be accomplished by the operator (informational)
Filtration - Media Design - (c) Tri-Media, Rapid Rate Gravity Filters
R309-525-15(4)(c) | Tri-media filters meet requirements (i) through (vii) below:
R309-525-15(4)(c)(i) | Total depth of filter bed is min. of 24 inches and max. of 30 inches
R309-525-15(4)(c)(ii) | All materials used to make up the filter bed are of such particle size and density that they will be effectively washed at backwash rates between 15 and 20 gpm/sf
R309-525-15(4)(c)(ii) | Materials will settle to reconstitute the bed to the normal gradation of coarse to fine in the direction of flow upon completion of backwashing
R309-525-15(4)(c)(iii) | The bottom layer is min. of four inches thick and consists of a material having an effective size ≤0.45 mm and uniformity coefficient ≤2.2
R309-525-15(4)(c)(iii) | The bottom layer thickness is reduced to three inches because it consists of a material having an effective size ≤0.25 mm and a uniformity coefficient ≤2.2
R309-525-15(4)(c)(iv) | The middle layer consists of silica sand having an effective size of 0.35 mm to 0.8 mm
R309-525-15(4)(c)(iv) | The middle layer has a uniformity coefficient ≤1.8
R309-525-15(4)(c)(v) | The top layer consists of clean crushed anthracite coal having an effective size of 0.45 mm to 1.2 mm, and a uniformity coefficient ≤1.85
R309-525-15(4)(c)(v) | The top layer consists of clean crushed anthracite coal having a uniformity coefficient ≤1.85
R309-525-15(4)(c)(vi) | Tri-media filters will be assigned a filter rate up to 6 gpm/sf (informational)
R309-525-15(4)(c)(vi) | Generally, if the bottom fine layer consists of a material having an effective size of 0.35 mm or less, a filtration rate of six gpm/sf can be assigned (informational)
R309-525-15(4)(c)(vii) | Each Tri-media filter is provided with equipment that continuously monitors turbidity in the filtered water
R309-525-15(4)(c)(vii) | The equipment is designed to initiate automatic backwash if the effluent turbidity exceeds 0.3 NTU
R309-525-15(4)(c)(vii) | If the filter turbidity exceeds one NTU, the filter will shut down
R309-525-15(4)(c)(vii) | In plants attended part-time, this shutdown will be accomplished automatically and be accompanied by an alarm
R309-525-15(4)(c)(vii) | In plants with full-time operators, a one NTU condition activates an alarm
R309-525-15(4)(c)(vii) | In plants with full-time operators, when a one NTU condition occurs, filter shutdown may then be accomplished by the operator (informational)
Filtration - Media Design - (d) Granulated Activated Carbon (GAC)
R309-525-15(4)(d) | Use of granular activated carbon media has received the prior approval of the Director
R309-525-15(4)(d) | Use of granular activated carbon meets the basic specifications for filter material given above
R309-525-15(4)(d)(i) | There is a provision for adding a disinfectant to achieve a suitable residual in the water following the filters and prior to distribution
R309-525-15(4)(d)(ii) | There is a means for periodic treatment of filter material for control of biological or other growths
R309-525-15(4)(d)(iii) | Facilities for carbon regeneration or replacement are provided
Filtration - Media Design - (e) Other Media Compositions and Configurations
R309-525-15(4)(e) | Filters consisting of materials or configurations not prescribed in this section will be considered on experimental data or available operation experience (informational)
Filtration - Support Media, Filter Bottoms and Strainer Systems
R309-525-15(5) | Filter media, support media, filter bottoms and strainer systems are compatible
R309-525-15(5) | Filter media, support media, filter bottoms and strainer will give satisfactory service at all times
Filtration - Support Media
R309-525-15(5)(a) | The design of support media will vary with the configuration of the filtering media and the filter bottom (informational)
R309-525-15(5)(a) | Support media and/or proprietary filter bottoms are reviewed on a case-by-case basis
Filtration - Filter Bottoms and Strainer Systems
R309-525-15(5)(b)(i) | Manifold type collection system design meets requirements (A) through (E) below:
R309-525-15(5)(b)(i)(A) | Minimize loss of head in the manifold and laterals
R309-525-15(5)(b)(i)(B) | Assure even distribution of washwater and even rate of filtration over the entire area of the filter
R309-525-15(5)(b)(i)(C) | Provide a ratio of the area of the final openings of the strainer system to the area of the filter of about 0.003
R309-525-15(5)(b)(i)(D) | Provide the total cross-sectional area of the laterals at about twice the total area of the final openings
R309-525-15(5)(b)(i)(E) | Provide the cross-sectional area of the manifold at 1.5 to 2 times the total area of the laterals
R309-525-15(5)(b)(ii) | Departures from these standards may be acceptable for high rate filter and for proprietary bottoms (informational)
R309-525-15(5)(b)(iii) | Porous plate bottoms are absent where calcium carbonate, iron, or manganese may clog them or with waters softened by lime
Filtration - Structural Details and Hydraulics
R309-525-15(6) | The filter structure is designed to provide (a) through (p) below:
R309-525-15(6)(a) | Vertical walls within the filter
R309-525-15(6)(b) | Filter walls are absent from protruding into the filter media
R309-525-15(6)(c) | Covered by superstructure
R309-525-15(6)(d) | Head room provided to permit normal inspection and operation
R309-525-15(6)(e) | Minimum water depth over the surface of the filter media of three feet, unless an exception is granted by the Director
R309-525-15(6)(f) | Maximum water depth above the filter media shall not exceed 12 feet
R309-525-15(6)(g) | Effluent is trapped to prevent backflow of air to the bottom of the filters
R309-525-15(6)(h) | Prevention of floor drainage from entering onto the filter by installation of a minimum four inch curb around the filters
R309-525-15(6)(i) | Prevention of flooding by providing an overflow or other means of control
R309-525-15(6)(j) | Maximum velocity of treated water in pipe and conduits to filters of two fps
R309-525-15(6)(k) | Cleanouts and straight alignment for influent pipes or conduits where solids loading is heavy or following lime-soda softening
R309-525-15(6)(l) | Washwater drain capacity to carry maximum flow
R309-525-15(6)(m) | Walkways around filters to be ≥24 inches wide
R309-525-15(6)(n) | Safety handrails or walls around filter areas adjacent to normal walkways
R309-525-15(6)(o) | Common wall is absent between filtered and unfiltered water (this requirement may be waived by the Director for small "package" type plants using metal tanks of sufficient thickness)
R309-525-15(6)(p) | Filtration to waste for each filter
Filtration - Backwash - Water Backwash Without Air
R309-525-15(7)(a) | Water backwash system is designed so that backwash water is not recycled to the head of the treatment plant unless it has been settled, as a minimum
R309-525-15(7)(a) | Water backwash systems, including tanks, pumps and pipelines, meet (i) through (xi) below:
R309-525-15(7)(a)(i) | Provide a minimum backwash rate of 15 gpm/sf, consistent with water temperatures and the specific gravity of the filter media
R309-525-15(7)(a)(i) | The design provides for adequate backwash with minimum media loss
R309-525-15(7)(a)(i) | Reduced rate of 10 gpm/sf may be acceptable for full depth anthracite/granular activated carbon filters (informational)
R309-525-15(7)(a)(ii) | Provide finished drinking water at the required rate from washwater tanks, a washwater pump, the high service main, or a combination
R309-525-15(7)(a)(iii) | Permit the backwashing of any one filter for minimum of 15 minutes
R309-525-15(7)(a)(iv) | Be capable of backwashing at least two filters, consecutively
R309-525-15(7)(a)(v) | Include a means of varying the filter backwash rate and time
R309-525-15(7)(a)(vi) | Include a washwater regulator or valve on the main washwater line to obtain the desired rate of filter wash with washwater valves or the individual filters open wide
R309-525-15(7)(a)(vii) | Include a rate of flow indicator, preferably with a totalizer on the main washwater line, located so that it can be easily read by the operator during the washing process
R309-525-15(7)(a)(viii) | Be designed to prevent rapid changes in backwash water flow
R309-525-15(7)(a)(ix) | Use only finished drinking water
R309-525-15(7)(a)(x) | Have washwater pumps in duplicate unless an alternate means of obtaining washwater is available
R309-525-15(7)(a)(xi) | Perform in conjunction with "filter to waste" system to allow filter to stabilize before introduction into clearwell
Filtration - Backwash - Backwash With Air Scouring
R309-525-15(7)(b) | If air scouring is provided in place of surface wash, requirements (i) through (xi) below are met:
R309-525-15(7)(b)(i) | Air flow for air scouring the filter is 3 to 5 scfm/sf of filter area when the air is introduced in the underdrain
R309-525-15(7)(b)(i) | A lower air rate is used when the air scour distribution system is placed above the underdrains
R309-525-15(7)(b)(ii) | A method for avoiding excessive loss of the filter media during backwashing is provided
R309-525-15(7)(b)(iii) | Air scouring is followed by a fluidization wash sufficient to restratify the media
R309-525-15(7)(b)(iv) | Air is free from contamination
R309-525-15(7)(b)(v) | Air scour distribution systems are placed below the media and supporting bed interface
R309-525-15(7)(b)(v) | If placed at the interface, the air scour nozzles are designed to prevent media from clogging the nozzles or entering the air distribution system
R309-525-15(7)(b)(vi) | Piping for the air distribution system avoids use of a flexible hose that will collapse when not under air pressure
R309-525-15(7)(b)(vi) | Piping for the air distribution system avoids use of a relatively soft material, which may erode at the orifice opening with the passage of air at high velocity
R309-525-15(7)(b)(vii) | Air delivery piping avoids passing down through the filter media
R309-525-15(7)(b)(vii) | Air delivery piping avoids any arrangement in the filter design that would allow short circuiting between the applied unfiltered water and the filtered water
R309-525-15(7)(b)(viii) | Design considers maintenance and replacement of air delivery piping
R309-525-15(7)(b)(ix) | When air scour is provided, the backwash water rate is variable and <8 gpm/sf unless operating experience shows that a higher rate is necessary to remove scoured particles from filter surfaces
R309-525-15(7)(b)(x) | The filter underdrains are designed to accommodate air scour piping when the piping is installed in the underdrain
R309-525-15(7)(b)(xi) | The provisions of Section R309-525-15(7)(a) (Backwash) are followed
Filtration - Surface Wash or Subsurface Wash
R309-525-15(8) | Surface wash or subsurface wash facilities are provided except for filters used exclusively for Fe or Mn removal
R309-525-15(8) | Washing that uses a system of fixed nozzles or a revolving-type apparatus meets (a) through (d) below:
R309-525-15(8)(a) | Provisions for water pressures of at least 45 psi
R309-525-15(8)(b) | A properly installed vacuum breaker or other approved device to prevent back-siphonage if connected to a finished drinking water system
R309-525-15(8)(c) | All washwater is finished drinking water
R309-525-15(8)(d) | Rate of flow of 2 gpm/sf of filter area with fixed nozzles or 0.5 gpm/sf with revolving arms
Filtration - Washwater Troughs
R309-525-15(9) | Washwater troughs are designed to meet requirements (a) through (e) below:
R309-525-15(9)(a) | The bottom elevation is above the maximum level of expanded media during washing
R309-525-15(9)(b) | A two inch freeboard is provided at the maximum rate of wash
R309-525-15(9)(c) | The top edge level and all edges of trough are at the same elevation
R309-525-15(9)(d) | Spacing is provided so that each trough serves the same number of square feet of filter areas
R309-525-15(9)(e) | Maximum horizontal travel of suspended particles to reach the trough is ≤3 feet
Filtration - Appurtenances
R309-525-15(10)(a) | Every filter is provided with (i) through (vii) below:
R309-525-15(10)(a)(i) | Sample taps or means to obtain samples from influent and effluent
R309-525-15(10)(a)(ii) | A gauge indicating loss of head
R309-525-15(10)(a)(iii) | A meter indicating rate-of-flow
R309-525-15(10)(a)(iii) | A modified rate controller that limits the rate of filtration to a maximum rate may be used (optional)
R309-525-15(10)(a)(iii) | However, equipment that simply maintains a constant water level on the filters is acceptable only if the rate of flow onto the filter is properly controlled (informational)
R309-525-15(10)(a)(iv) | A continuous turbidity monitoring device where the filter is to be loaded at a rate >3 gpm/sf
R309-525-15(10)(a)(v) | Provisions for draining the filter to waste with appropriate measures for backflow prevention (see R309-525-23)
R309-525-15(10)(a)(vi) | Wall sleeves providing access to the filter interior at several locations for sampling or pressure sensing
R309-525-15(10)(a)(vii) | A 1.0 inch to 1.5 inch diameter pressure hose and storage rack at the operating floor for washing filter walls
Filtration - Miscellaneous
R309-525-15(11) | Roof drains avoid discharge into filters or basins and conduits preceding the filters
In-Plant Finished Drinking Water Storage - General
R309-525-16(1) | Plant storage meets applicable design standards of R309-545 and requirements (a) and (b) below:
R309-525-16(1)(a) | Backwash water tanks are sized in conjunction with available pump units and finished water storage to provide the backwash water required by R309-525-15(7)
R309-525-16(1)(a) | Backwashing of several filters in rapid succession has been considered
R309-525-16(1)(b) | Clearwell storage is sized in conjunction with distribution system storage to relieve the filters from having to follow fluctuations in water use and meets (i) through (iii) below:
R309-525-16(1)(b)(i) | When finished water storage is used to provide the contact time for chlorine (see R309-520-10(1)(f), especially sub-section (f)(iv)), special attention is given to size and baffling
R309-525-16(1)(b)(ii) | To ensure adequate chlorine contact time, sizing of the clearwell includes extra volume to accommodate depletion of storage during the nighttime for intermittently operated filtration plants with automatic high service pumping from the clearwell during non-treatment hours
R309-525-16(1)(b)(iii) | An overflow and vent are provided
R309-545-14 | Recommend meeting design requirements of R309-545 (especially for access)
In-Plant Finished Drinking Water Storage - Adjacent Compartments
R309-525-16(2) | For finished drinking water stored or conveyed in a compartment adjacent to unsafe water, the two compartments are separated by more than a single wall
R309-525-16(2) | The Director may grant an exception to this requirement for small "package" treatment plants using metal tanks of sufficient wall thickness (informational)
In-Plant Finished Drinking Water Storage - Basins and Wet Wells
R309-525-16(3) | Receiving basins and pump wet wells for finished drinking water are designed as drinking water storage structures (see Section R309-545)
Miscellaneous Plant Facilities - Laboratory
R309-525-17(1) | Sufficient laboratory equipment is provided to assure proper operation and monitoring of the water plant and includes items (a) through (m) below:
R309-525-17(1)(a) | One floc testing apparatus with illuminated base and variable speed stirrer
R309-525-17(1)(b) | Ten 1000 ml Griffin beakers (plastic is highly recommended over glass to prevent breakage)
R309-525-17(1)(c) | One 1000 ml graduated cylinder (plastic is highly recommended over glass to prevent breakage)
R309-525-17(1)(d) | pH test strips (6.0 to 8.5)
R309-525-17(1)(e) | Five wide mouth 25 ml Mohr pipets
R309-525-17(1)(f) | One triple beam, single pan or double pan balance with 0.1 g sensitivity and 2000 g capacity (using attachment weights)
R309-525-17(1)(g) | DPD chlorine test kit
R309-525-17(1)(h) | Bench-top turbidimeter
R309-525-17(1)(i) | Five 1000 ml reagent bottles with caps
R309-525-17(1)(j) | Dish soap
R309-525-17(1)(k) | Brush (2 3/4 inch diameter by 5 inch)
R309-525-17(1)(l) | One platform scale 1/2 lb sensitivity, 100 lb capacity
R309-525-17(1)(m) | Book - Simplified Procedures for Water Examination, AWWA Manual M12
Miscellaneous Plant Facilities - Continuous Turbidity Monitoring and Recording Equipment
R309-525-17(2) | Continuous turbidity monitoring and recording facilities are located as specified in R309-215-9
Miscellaneous Plant Facilities - Sanitary and Other Conveniences
R309-525-17(3) | A treatment plant is provided with finished drinking water, lavatory, and toilet facilities unless such facilities are otherwise conveniently available
R309-525-17(3) | Plumbing conforms to the Utah Plumbing Code and is installed to prevent contamination of a public water supply
Sample Taps
R309-525-18 | Sample taps are provided so water samples can be taken at appropriate locations in each unit operation of treatment
R309-525-18 | Taps are consistent with sampling needs
R309-525-18 | Petcock type taps are absent
R309-525-18 | Taps used for obtaining samples for bacteriological analysis are smooth-nosed type without interior or exterior threads
R309-525-18 | Mixing-type taps are absent
R309-525-18 | Screens are absent on taps
R309-525-18 | Aerator or other such appurtenances are absent on taps
Operation and Maintenance Manuals
R309-525-19 | Operation and maintenance manuals are prepared for the treatment plant and are acceptable by the Director
R309-525-19 | O&M manuals are usable and easily understood
R309-525-19 | O&M manuals describe normal operating procedures, maintenance procedures and emergency procedures
Operator Instruction
R309-525-20 | Provisions are made for operator instruction at the start-up of a plant
Safety
R309-525-21 | All facilities are designed and constructed with regard for safety, comfort, and convenience
R309-525-21 | At a minimum, all applicable requirements of Utah Occupational Safety and Health Act (UOSHA) are adhered to
Disinfection Prior to Use
R309-525-22 | Piping is disinfected according to AWWA C651-05 Disinfecting Water Mains
R309-525-22 | Tanks are disinfected according to AWWA C652-02 Disinfection of Water Storage Facilities
R309-525-22 | Treatment plants are disinfected according to AWWA C653-03 Disinfection of Water Treatment Plants
Disposal of Treatment Plant Waste
R309-525-23 | Provisions are made for proper disposal of water treatment plant waste such as sanitary, laboratory, sludge, and filter backwash water
R309-525-23 | All waste discharges and treatment facilities meet the requirements of the plumbing code
R309-525-23 | All waste discharges and treatment facilities meet the requirements of the Utah Department of Environmental Quality
R309-525-23 | All waste discharges and treatment facilities meet the requirements of the Utah Department of Health
R309-525-23 | All waste discharges and treatment facilities meet requirements of the United States Environmental Protection Agency
R309-525-23 | All waste discharges and treatment facilities meet requirements of Rules for Onsite Wastewater Disposal Systems, Utah Administrative Code R317-4
R309-525-23 | All waste discharges and treatment facilities meet requirements of Water Quality Rules, UAC R317
R309-525-23 | All waste discharges and treatment facilities meet requirements of Solid & Hazardous Waste Rules, UAC R315
R309-525-23 | In locating waste disposal facilities, consideration is given to preventing potential contamination of a water supply as well as breach or damage due to environmental factors
Other Considerations
R309-525-24 | Consideration is given to design requirements of other federal, state, and local regulatory agencies for such items as safety requirements, special designs for handicapped, plumbing & electrical codes, construction in flood plains, etc.
Operation and Maintenance
R309-525-25(1) | All chemicals added to water intended for human consumption are suitable for drinking water use
R309-525-25(1) | All chemicals added to water comply with ANSI/NSF Standard 60
R309-525-25(2) | Director has approved chemical addition facilities and chemical type for all chemicals or other substances added to public water supplies
R309-525-25(2) | The primary coagulant may not be changed without prior approval from the Director (prohibition)
R309-525-25(2) | Director will be notified prior to the changing of primary coagulant type
R309-525-25(2) | Director has required documentation to verify that sufficient testing and analysis have been done
R309-525-25(3) | Stable flow rates are maintained through the filters during operation of a conventional surface water treatment plant
R309-525-25(4) | All instrumentation needed to verify that treatment processes are sufficient are properly calibrated and maintained, including turbidimeters
DDW Internal Plan Review Requirements for Surface Water Treatment Plants
N/A | Describe the source (name/source ID/type), water quality concerns, and the historical data that have been reviewed regarding source flow range, turbidity range, and source water bin classification data (if applicable)
N/A | Identify the treatment facility name and ID (same as the name and ID listed in SDWIS database).
N/A | Describe treatment type (e.g., conventional, membrane filtration, direct filtration, bag & cartridge filtration), process and technology (e.g., pH adjustment, coagulation, flocculation, sedimentation, disinfection by chlorine/chlorine dioxide/UV/ozone, clear well). Include manufacturer/brand/model info for package plant.
N/A | If applicable, describe the pre-treatment process (e.g., pre-oxidation by adding chlorine).
N/A | Describe the disinfection process in detail (e.g., pre-/post-chlorination, other disinfection processes). Include disinfection CT estimates for each treatment process, overall CT through the plant, and parameters used in the CT calculations.
N/A | If applicable, describe pilot test/bench top test (e.g., procedures, parameters, duration, results). Describe what results were used to determine pre-treatment, optimal dose, and the reason for selecting a specific pre-treatment process.
N/A | State specific treatment goals for Giardia, Crypto and virus (e.g., a minimum of 4-log virus inactivation/removal). Describe the proposed strategy in meeting these goals.
N/A | State the treatment credits that are (or are anticipated to be) granted for Giardia, virus, and Crypto. Describe the credits by process in sequence.
N/A | If the design includes a backwash water supply line and/or a plant utility water supply line, check whether they are connected to finished water. If yes, verify that these water supply lines are designed to prevent backflow and backpressure (i.e., no cross connection; having an approved backflow prevention assembly, an air gap, sufficient elevation difference, acceptable block and bleed manifold, etc.).
N/A | Describe the number of treatment trains, capacity of each train, and the overall design capacity of the treatment plant. If a surface water WTP is designed with a single train and lacks the redundancy per in R309-525-5, state the justification in the Plan Approval (PA)/Operating Permit (OP) for allowing a single train design. [The redundant train typically is not counted toward the WTP design capacity.]
N/A | Verify that there is no uncontrolled bypass line. [This is the major difference between the surface water and inorganics/organics WTPs. Untreated surface water is NOT allowed to bypass the treatment processes to be blended with finished water.]
N/A | Describe the waste stream(s) (e.g., backwash wastewater, sludge, brine) and how they will be handled. Verify and state whether the water system has a legal means to dispose these waste types. Include the waste/wastewater authority (e.g., Division of Water Quality, local sewer authority) in the cc list.
N/A | Describe whether ANSI/NSF 61 certification exists for the proposed treatment process/unit (except conventional and direct filtration plants).
N/A | Describe all chemicals that will be used for the proposed treatment processes. State whether these chemicals meet the ANSI/NSF 60 standard.
N/A | If applicable, address “simultaneous compliance” concerns. Describe whether the treated water and/or waste stream from the proposed treatment facility may result in unintended consequences in the distribution system or the environment. [For example, the finished water produced from a reverse osmosis (RO) WTP may cause corrosion or lead/copper MCL exceedance in the distribution system; the brine of RO reject stream may not be legally disposed.]
N/A | Plan Approval (PA) letters for surface water WTPs should include the following information:
N/A | (a) Specify “water quality data” that are required to show WTP performance before issuing a WTP OP. Customize the “water quality data” item in the generic Operating Permit (OP) checklist to include the following information:
N/A | • Specific parameters to be sampled (e.g., turbidity, minimum chlorine residual)
N/A | • Sampling locations (e.g., raw water, after filters, after clear well)
N/A | • Frequency of sampling (e.g., the highest turbidity reading at 4-hour intervals, daily turbidity sample at least one day apart for very small water systems)
N/A | • Number of before and after sample sets (e.g., 4 sets of before & after turbidity data, 7 days of 4-hour turbidity readings)
N/A | (b) Obtain the preliminary monitoring and reporting information from the Rules Section. Provide it to PWS (include with PA) for informational purposes. [The preliminary monitoring and reporting information is important if a WTP project includes PLC and SCADA programming prior to completion of the project or requesting OP.]
N/A | The Operating Permit (OP) letter must include the monitoring schedule follow-up paragraph.
N/A | Consult with the Rules Section staff.
N/A | • Surface water monthly report & customized report template for each WTP
N/A | • Disinfection
N/A | • WQ data review & WTP monitoring schedule
N/A | • If needed, surface water technical assistance and federal regulations