## Chlorine Dioxide Checklist
Disinfection: Chlorine Dioxide |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (Note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-520-6(1)(a) | Continuous disinfection is provided for all ground water sources that do not continuously meet microbiological standards
R309-520-6(1)(a) | Intermittent or batch disinfection is not acceptable alternative to continuous disinfection (prohibition)
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy physical deficiencies
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy sources susceptible to surface water influence
R309-520-6(1)(b) | Purpose of disinfection is other than to mask ongoing contamination
R309-520-6(1)(b) | Purpose of disinfection is other than use as a substitute for correcting deficiencies
R309-520-6(1)(c) | If continuous disinfection required, disinfect. equip. can be isolated/serviced wo/ allowing untreated water to enter dist. sys.
R309-520-6(1)(c) | Discharge of untreated water avoids environmental or property damage
R309-520-6(2) | Chemicals added to drinking water (chlorine, chloramines, hypochlorite solutions, chlorine dioxide) meet ANSI/NSF 60
R309-520-6(3)(a) | Surface water & GWUDI filtered by conventional SW treatment or alternative SW treatment & disinfected per R309-200-7
R309-520-6(3)(b) | If microbiological treatment is required for a ground water source, disinfection without filtration is provided
R309-520-6(4)(a) | Disinfectant contact time considers pH, NH3, taste-producing substances, temp, biological quality & other pertinent factors
R309-520-6(4)(b) | Design minimizes formation of disinfection byproducts
R309-520-6(4)(c) | Treatment of ground water sources provides sufficient CT to achieve min. of 4-log virus inactivation and/or removal
R309-520-6(4)(d) | Point of application for disinfectants located to achieve required disinfection CT prior to first service connection
R309-520-6(5) | Disinfection installations sited to permit convenient access during operation period
R309-520-6(5) | Installation site considers possible danger to nearby population
R309-520-6(5) | Installation site considers possible jeopardy from seismic fault zones
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
N/A | Project will resolve existing physical deficiencies
Additional General Requirements for Chlorine Dioxide
R309-520-10 | Effect of chlorine dioxide on sensitive populations was considered
R309-520-10 | Chlorine dioxide will not be used as a secondary disinfectant
R309-520-10 | Chlorine dioxide residuals and byproducts will be monitored in the distribution system
R309-520-10 | Public notified of effect of chlorine dioxide residual in distribution system on sensitive populations
Pre-design Proposal
R309-520-10(1) | Proposal to use chlorine dioxide discussed with DDW prior to plan submittal
R309-520-10(1) | Written proposal to use chlorine dioxide submitted to the Director includes items (a) through (d) below:
R309-520-10(1)(a) | Make, model, and specifications for chlorine dioxide generator
R309-520-10(1)(b) | References of other potable water installations in the U.S. that use the proposed unit
R309-520-10(1)(c) | Information about O&M training program
R309-520-10(1)(d) | Expected total applied dosage of chlorine dioxide and other disinfectants, points of application for all disinfectants, type and amount of residuals, and expected by-products in the distribution system
Chlorine Dioxide Generators
R309-520-10(2)(a) | Chlorine dioxide generation is designed to be efficient compared to the industry standard
R309-520-10(2)(a) | Excess chlorine production is minimized
R309-520-10(2)(b) | Generator does not produce chlorine dioxide solution in excess of 6,000 mg/L
R309-520-10(2)(c) | Design includes capability to measure concentrations of chlorine dioxide, chlorite, chlorate, and free chlorine of the solution leaving the generator
R309-520-10(2)(d) | Chlorine dioxide generator equipped with chlorine dioxide analyzer to measure strength of the solution leaving the generator
R309-520-10(2)(e) | Generator uses other than solid chloride (solid chloride prohibited)
Chlorine Dioxide Feed System
R309-520-10(3)(a)(i) | Fiberglass reinforced vinyl ester plastic (FRP) or high density linear polyethylene (HDLPE) tanks with no insulation specified
R309-520-10(3)(a)(ii) | Centrifugal pumps have Teflon packing material
R309-520-10(3)(a)(ii) | Pump motors are totally enclosed
R309-520-10(3)(a)(ii) | Pump motors are fan cooled
R309-520-10(3)(a)(ii) | Pump motors are equipped with permanently sealed bearings
R309-520-10(3)(a)(ii) | Pump motors are equipped with double mechanical seals or other means to prevent leakage
R309-520-10(3)(a)(iii) | Piping material is PVC, vinyl ester, or Teflon
R309-520-10(3)(a)(iii) | Piping is other than carbon steel or stainless steel (carbon & stainless steel piping prohibited)
R309-520-10(3)(a)(iv) | Non-transparent reactor has glass view port
R309-520-10(3)(a)(v) | Chemical feed, dilution water, and chlorine dioxide solution lines have flow monitoring
R309-520-10(3)(a)(vi) | Means to verify calibrated feed flow provided for each application feed point
R309-520-10(3)(a)(vii) | Air contact with chlorine dioxide solution is controlled to limit potential for explosion
R309-520-10(3)(a)(viii) | Chlorine solution concentration will be less than 30%
Chlorine Dioxide Storage and Operating Area
R309-520-10(3)(b) | Chlorite storage and chlorine dioxide day tank areas meet requirements of (i) through (xvii) below:
R309-520-10(3)(b)(i) | Chlorine dioxide facility is located in separate room from other water treatment plant operating areas
R309-520-10(3)(b)(ii) | Chlorine dioxide area has ventilation system separate from other operating areas
R309-520-10(3)(b)(iii) | Chlorine dioxide facility area is vented to maintain ambient air chlorine dioxide concentrations below Permissible Exposure Limit and meets requirements (A) through (D) below:
R309-520-10(3)(b)(iii)(A) | Vent fan takes suction near the floor
R309-520-10(3)(b)(iii)(A) | Vent fan is far as practical from door
R309-520-10(3)(b)(iii)(A) | Vent fan is far as practical form air inlet
R309-520-10(3)(b)(iii)(A) | Vent discharge located not to contaminate air inlets
R309-520-10(3)(b)(iii)(B) | Air inlets are near the ceiling
R309-520-10(3)(b)(iii)(C) | Air inlets and outlets are louvered
R309-520-10(3)(b)(iii)(D) | Separate switches for fans are located outside and near the facility entrance
R309-520-10(3)(b)(iv) | Chlorine dioxide facility is constructed of non-combustible materials such as concrete
R309-520-10(3)(b)(v) | Ambient air chlorine dioxide sensor is in the vicinity of the chlorine dioxide operating area
R309-520-10(3)(b)(v) | Ambient air chlorine dioxide sensor readouts and alarm or warning light is audible/visible in the operating area and outside the door to the operating area
R309-520-10(3)(b)(v) | Design includes distinguishing audible alarms triggered by ambient air chlorine dioxide sensor readings
R309-520-10(3)(b)(vi) | Observation window for viewing operating area from outside is provided
R309-520-10(3)(b)(vii) | Manual light switches for operating area are located outside of the door
R309-520-10(3)(b)(viii) | Emergency shower and eyewash are located outside and close to operating area door
R309-520-10(3)(b)(ix) | Emergency shutoff for water flow to generator is located outside of the operating area
R309-520-10(3)(b)(x) | Design minimizes possibility of chlorite leaks
R309-520-10(3)(b)(xi) | Chlorite tank and chlorine dioxide solution tank are vented to outdoors
R309-520-10(3)(b)(xi) | Chlorite tank and chlorine dioxide solution tank are vented away from operating areas
R309-520-10(3)(b)(xii) | Gaseous chlorine feed to chlorine dioxide generator enters chlorine dioxide facility area through vacuum-feed lines
R309-520-10(3)(b)(xiii) | Floor of chlorine dioxide facility slopes to a sump
R309-520-10(3)(b)(xiv) | Open drains in the chlorine dioxide operating area are absent
R309-520-10(3)(b)(xv) | Chlorine dioxide storage & chlorine dioxide solutions have secondary containment w/ sumps to hold entire volume of vessels
R309-520-10(3)(b)(xv) | Containment prevents chlorine dioxide solutions from entering the rest of the operating area
R309-520-10(3)(b)(xvi) | Wash-down water is provided in operating area
R309-520-10(3)(b)(xvii) | Operating area is designed to avoid direct exposure to sunlight
R309-520-10(3)(b)(xvii) | Operating area is designed to avoid direct exposure to UV light
R309-520-10(3)(b)(xvii) | Operating area is designed to avoid direct exposure to excessive heat
Other Design Criteria
R309-520-10(4)(a) | Secondary containment is provided at bulk delivery transfer point
R309-520-10(4)(a) | Sump is provided at bulk delivery transfer point
R309-520-10(4)(a) | Wash-down water is provided at bulk delivery transfer point
R309-520-10(4)(a) | Shower is provided at bulk delivery transfer point
R309-520-10(4)(a) | Eyewash is provided at bulk delivery transfer point
R309-520-10(4)(b) | Finished water is used for chlorine dioxide generation
R309-520-10(4)(c) | Finished water line to chlorine dioxide generator is protected with high hazard backflow assembly
R309-520-10(4)(d) | Water supply is provided near storage and handling area for clean up
R309-520-10(4)(e) | Parts of chlorine dioxide system in contact with strong oxidizing or acid solutions are of inert material
R309-520-10(4)(f) | Design allows chlorine dioxide operation to be shut off remotely from location outside of chlorine dioxide operating area
Operation and Maintenance
R309-520-10(5)(a) | Combustible/reactive materials (acids, reduced metals, organic material) are absent from chlorine dioxide operating area
R309-520-10(5)(b) | Chemicals are stored in clean, closed, non-translucent containers
R309-520-10(5)(c) | Personal protective equipment is stored nearby, outside of chlorine dioxide facility area
R309-520-10(5)(c) | First aid kit is stored nearby, outside of chlorine dioxide facility area
R309-520-10(5)(d) | Temperature of chlorine dioxide operating area is maintained between 60° and 100°F
R309-520-10(5)(e) | After delivery, chlorite solutions are allowed to equalize with ambient temperature of operating area to avoid stratification
R309-520-10(5)(f) | O&M manual includes operator safety and emergency response procedures
R309-520-10(5)(f) | Personnel get ongoing operator safety and emergency response procedure training
R309-520-10(5)(g) | Waste disposed of according to existing solid and hazardous waste regulations
R309-520-10(5)(h) | Operating area inspected daily for chlorite spills and solid chlorite buildup
R309-520-10(5)(h) | Daily inspection log is maintained
R309-520-10(5)(i) | Chlorite leaks and solid chlorite buildup cleaned up and disposed of immediately
R309-520-10(5)(j) | Solid chlorite washed down before removal
R309-520-10(5)(k) | Chlorine dioxide facility ventilation system is operated to maintain ambient air chlorine dioxide concentrations below Permissible Exposure Limit
R309-520-10(5)(l) | Audible alarms programmed to alert water treatment plant personnel when ambient air chlorine dioxide sensor in the chlorine dioxide operating area detects chlorine dioxide concentration above Permissible Exposure Limit and Short Term Exposure Limit