## Ozone Checklist
Disinfection: Ozone |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-520-6(1)(a) | Continuous disinfection is provided for all ground water sources that do not continuously meet microbiological standards
R309-520-6(1)(a) | Intermittent or batch disinfection is not acceptable alternative to continuous disinfection (prohibition)
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy physical deficiencies
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy sources susceptible to surface water influence
R309-520-6(1)(b) | Purpose of disinfection is other than to mask ongoing contamination
R309-520-6(1)(b) | Purpose of disinfection is other than use as a substitute for correcting deficiencies
R309-520-6(1)(c) | If continuous disinfection required, disinfect. equip. can be isolated/serviced wo/ allowing untreated water to enter dist. sys.
R309-520-6(1)(c) | Discharge of untreated water avoids environmental or property damage
R309-520-6(2) | Chemicals added to drinking water (chlorine, chloramines, hypochlorite solutions, chlorine dioxide) meet ANSI/NSF 60
R309-520-6(3)(a) | Surface water & GWUDI filtered by conventional SW treatment or alternative SW treatment & disinfected per R309-200-7
R309-520-6(3)(b) | If microbiological treatment is required for a ground water source, disinfection without filtration is provided
R309-520-6(4)(a) | Disinfectant contact time considers pH, NH3, taste-producing substances, temp, biological quality & other pertinent factors
R309-520-6(4)(b) | Design minimizes formation of disinfection byproducts
R309-520-6(4)(c) | Treatment of ground water sources provides sufficient CT to achieve min. of 4-log virus inactivation and/or removal
R309-520-6(4)(d) | Point of application for disinfectants located to achieve required disinfection CT prior to first service connection
R309-520-6(5) | Disinfection installations sited to permit convenient access during operation period
R309-520-6(5) | Installation site considers possible danger to nearby population
R309-520-6(5) | Installation site considers possible jeopardy from seismic fault zones
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
N/A | Project will resolve existing physical deficiencies
General Requirements for Ozone Disinfection
R309-520-9(1)(a) | Ozone can not be used as a secondary disinfectant (prohibition)
R309-520-9(1)(a) | Disinfectant other than ozone is used if min. disinfection residual is required in distribution system
R309-520-9(1)(a) | Ozone is used for taste and odor control, oxidation of inorganic and organic compounds, or for enhanced performance of other water treatment processes, such as micro-flocculation and filtration
R309-520-9(1)(b) | Pilot or bench-scale studies conducted for surface water treatment
R309-520-9(1)(b) | Pilot or bench-scale studies not conducted for surface water treatment because sufficient data are available from other studies performed on the same water source
R309-520-9(1)(b) | Studies done to determine initial ozone demand, rate of ozone decay, min. and max. ozone dosages for range of water conditions for CT compliance, and ozone dosage required for other desired benefits
R309-520-9(1)(b) | Pilot or bench-scale studies take into account seasonal and other variations of source water
R309-520-9(1)(b) | Plans for pilot or bench-scale studies reviewed and accepted by the Director prior to beginning the studies
R309-520-9(2)(a) | Ozone system designed with backup capability to achieve required inactivation with one generator out of service
R309-520-9(2)(b) | Ozone generator housed in enclosed, temperature-controlled building
R309-520-9(2)(b) | Adequate building ventilation is provided (≥6 air changes per hour)
R309-520-9(2)(c) | Ozone generator is medium- or high-frequency type
R309-520-9(2)(d) | Power supply units for ozone generators have a backup electrical power source or alternate primary disinfection system in case of electrical power outage
R309-520-9(2)(e) | Ozone generator is water cooled with max. increase of cooling water temp. of 10°F (5.6°C)
R309-520-9(2)(e) | Cooling water is treated to minimize corrosion, scaling, and microbiological fouling of water-side of tubes (if necessary)
R309-520-9(2)(e) | Closed-loop cooling water system is used to assure proper water conditions are maintained (optional; not required)
R309-520-9(2)(e) | Power supply units to ozone generators are water cooled (optional; not required)
Ozone Generator Feed Gas
R309-520-9(3)(a) | Feed gas is air, vaporized high purity liquid oxygen, or oxygen-enriched air
R309-520-9(3)(a) | Oxygen is generated on site or delivered in bulk
R309-520-9(3)(a) | Oxygen-enriched air is typically generated on site (recommendation)
R309-520-9(3)(b) | Feed gas system design ensures that feed gas max. dew point of -76°F (-60°C) is never exceeded
Liquid Oxygen Feed Gas Systems
R309-520-9(3)(c)(i) | Liquid oxygen storage tanks are sized to provide min. 7-day supply to ozone generators at max. operating rate
R309-520-9(3)(c)(ii) | Two or more vaporizers are provided to convert liquid oxygen to gaseous form
R309-520-9(3)(c)(ii) | Vaporizers are capable of maintaining oxygen flow at min. design air temperature with one unit on standby
R309-520-9(3)(c)(iii) | Liquid oxygen storage tanks and system comply with Chapter 40, Oxidizers, 2006 International Fire Code
Air or Oxygen-Enriched-Air Feed Gas Systems
R309-520-9(3)(d)(i) | Two or more air compressors are provided to supply air
R309-520-9(3)(d)(i) | Capacity of compressors designed to meet demand during max. ozone production plus other compressed air uses at treatment plant with largest compressor out of service
R309-520-9(3)(d)(ii) | Entrainment separators, refrigeration dryers, desiccant dryers, and filters specified as necessary to provide sufficiently dried, dust-free, oil-free gas to ozone generators
R309-520-9(3)(d)(ii) | Multiple entrainment separators, refrigeration dryers, desiccant dryers, and filters are specified to prevent interruption of ozone generation
Ozone Contactors
R309-520-9(4)(a) | Ozone contactor consists of 2 or more chambers to provide for introduction of ozone into water and provide for contact time
R309-520-9(4)(a) | In a water treatment plant, ozone can be introduced in raw water or later in the treatment process (options)
R309-520-9(4)(a) | Ozone contactor is a closed vessel kept under less than atmospheric pressure to prevent escape of ozone gas
R309-520-9(4)(a) | Construction materials are ozone-resistant to prevent premature failure of contactor
R309-520-9(4)(b) | Alternative 1: Ozone gas injected into water under positive pressure using porous-tube or dome bubble diffusers
R309-520-9(4)(b) | Alternative 2: Ozone gas injected into water using side stream injection under negative pressure generated by a venturi
R309-520-9(4)(c) | Ozone contactor designed to achieve min. transfer efficiency of 85%
R309-520-9(4)(d) | Multiple sample points are provided in the ozone contactor to enable sampling of treated water to determine an accurate measure of concentration to be used in CT calculation
R309-520-9(4)(e) | Minimum disinfection contact time is ten minutes (recommendation)
R309-520-9(4)(f) | Ozone contactors have provisions for cleaning, maintenance, and drainage
R309-520-9(4)(f) | Contactor chamber is equipped with access hatchway or other means of entry
R309-520-9(4)(g) | Ozone contactor has an emergency off-gas pressure/vacuum relief system
R309-520-9(4)(h) | Ozone level safety system is provided at the ozone contactor for compliance with OSHA standards for worker safety
R309-520-9(4)(h) | Ozone levels in gas space above treated water that has exited contactor will not exceed OSHA’s 8-hr 0.1 ppm exposure limit
R309-520-9(4)(h) | Ozone level safety system may be ozone residual quenching system using a chemical to destroy remaining ozone in the water or a monitoring system providing sufficient time to lower the residual ozone level in the water to an acceptable level by natural decay
R309-520-9(4)(h) | A chemical used to quench residual ozone shall comply with ANSI/NSF 60
Off-Gas Destruction Units
R309-520-9(5)(a) | System for treating final off-gas from each ozone contactor to safety standards is provided
R309-520-9(5)(a) | System uses either thermal destruction or catalytic destruction
R309-520-9(5)(a) | Two destruction units, each capable of handling entire off-gas flow, are provided
R309-520-9(5)(b) | Exhaust blowers are provided to draw off-gas from the contactor to the destruction units
R309-520-9(5)(c) | Provisions made to drain water from condensation in off-gas piping and protect destruction units and piping from moisture or other impurities
R309-520-9(5)(d) | Maximum allowable ozone concentration in the gas discharge from a destruction unit is 0.1 ppm by volume
R309-520-9(5)(d) | Provision made for temporary transient concentration spikes that exceed 0.1 ppm
Piping Connections
R309-520-9(6)(a) | Ozone’s nature as a strong oxidant was considered when specifying piping materials for ozone service
R309-520-9(6)(a) | Only low carbon 304L and 316L stainless steel specified for ozone gas service (general recommendation)
R309-520-9(6)(b) | Welded connections for ozone service piping provided (if possible)
R309-520-9(6)(b) | Threaded connections for ozone service piping avoided (recommendation)
R309-520-9(6)(b) | Connections with meters, valves, and other equipment made with flanged joints with ozone-resistant gaskets
R309-520-9(6)(c) | Positive-closing 90° turn isolation valve, or equivalent, provided in piping between ozone generator and contactor to prevent moisture from reaching generator during shutdowns
Instrumentation and Monitoring
R309-520-9(7)(a) | Flow meter is provided to measure flow rate of water being treated
R309-520-9(7)(a) | Temperature gauge or transmitter is provided to measure temperature of water being treated
R309-520-9(7)(a) | pH is measured to indicate changes in water being treated
R309-520-9(7)(b) | Gas analyzer is provided on gaseous ozone feed line going to ozone injection point
R309-520-9(7)(b) | Flow meter is provided on gaseous ozone feed line going to ozone injection point
R309-520-9(7)(b) | Temperature measurement is provided on gaseous ozone feed line going to ozone injection point
R309-520-9(7)(c) | Ozone aqueous residual analyzer is provided to measure ozone residual concentration in water being treated to determine CT credit
R309-520-9(7)(d) | Ozone gas analyzer is provided on gas discharge of each ozone destruction unit or combined vent gas discharge to determine exiting ozone concentration
R309-520-9(7)(e) | Ambient ozone monitors installed in vicinity of ozone generators
R309-520-9(7)(e) | Ambient ozone monitors installed in vicinity of ozone contactors
R309-520-9(7)(e) | Ambient ozone monitors installed in vicinity of ozone destruction units
R309-520-9(7)(e) | Ambient ozone monitors installed in other areas where ozone gas may accumulate
R309-520-9(7)(f) | Continuous dew-point monitor provided on feed gas line to ozone generators
R309-520-9(7)(g) | Instrumentation provided as necessary to monitor feed gas system performance and protect equipment
R309-520-9(7)(g) | Instrumentation provided as necessary to monitor ozone generators’ performance and protect equipment
R309-520-9(7)(g) | Instrumentation provided as necessary to monitor power supply units’ performance and protect equipment
R309-520-9(7)(g) | Instrumentation provided as necessary to monitor cooling water performance and protect equipment
Alarms and Shutdowns
R309-520-9(8)(a) | Ambient ozone monitor is provided
R309-520-9(8)(b) | Design includes alarms and shutdowns
Safety
R309-520-9(9)(a) | Training provided to ozone system operators by manufacturers of ozone equipment or other professionals experienced in ozone treatment
R309-520-9(9)(b) | Appropriate signs are installed around ozone and liquid oxygen equipment to warn operators, emergency responders, and others of potential danger
R309-520-9(9)(c) | Means provided to reduce residual ozone levels in ozone contactor/other equipment to safe levels prior to entry for repair, maintenance, or emergency
Operation and Maintenance
R309-520-9(10)(a) | Ambient ozone monitor activates alarm when ozone level exceeds 0.1 ppm
R309-520-9(10)(a) | Ozone generator designed to shut down when ambient ozone levels exceed 0.3 ppm in vicinity of ozone generator/contactor
R309-520-9(10)(a) | Ozone ambient monitor activates local audible alarm and/or flashing light in addition to alarm at operator control sys. panel
R309-520-9(10)(b) | Alarm/shut down provided to prevent dew point of feed gas exceeding max. of -76°F (-60°C)
R309-520-9(10(c) | Alarms and shut downs are programmed based on pressure gauges, flow meters, and power meters to protect feed gas system, ozone generators, power supply units, and cooling water system