## UV Checklist
Disinfection: Ultraviolet Light |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-520-6(1)(a) | Continuous disinfection is provided for all ground water sources that do not continuously meet microbiological standards
R309-520-6(1)(a) | Intermittent or batch disinfection is not acceptable alternative to continuous disinfection (prohibition)
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy physical deficiencies
R309-520-6(1)(b) | Purpose of disinfection is other than to remedy sources susceptible to surface water influence
R309-520-6(1)(b) | Purpose of disinfection is other than to mask ongoing contamination
R309-520-6(1)(b) | Purpose of disinfection is other than use as a substitute for correcting deficiencies
R309-520-6(1)(c) | If continuous disinfection required, disinfect. equip. can be isolated/serviced wo/ allowing untreated water to enter dist. sys.
R309-520-6(1)(c) | Discharge of untreated water avoids environmental or property damage
R309-520-6(2) | Chemicals added to drinking water (chlorine, chloramines, hypochlorite solutions, chlorine dioxide) meet ANSI/NSF 60
R309-520-6(3)(a) | Surface water & GWUDI filtered by conventional SW treatment or alternative SW treatment & disinfected per R309-200-7
R309-520-6(3)(b) | If microbiological treatment is required for a ground water source, disinfection without filtration is provided
R309-520-6(4)(a) | Disinfectant contact time considers pH, NH3, taste-producing substances, temp, biological quality & other pertinent factors
R309-520-6(4)(b) | Design minimizes formation of disinfection byproducts
R309-520-6(4)(c) | Treatment of ground water sources provides sufficient CT to achieve min. of 4-log virus inactivation and/or removal
R309-520-6(4)(d) | Point of application for disinfectants located to achieve required disinfection CT prior to first service connection
R309-520-6(5) | Disinfection installations sited to permit convenient access during operation period
R309-520-6(5) | Installation site considers possible danger to nearby population
R309-520-6(5) | Installation site considers possible jeopardy from seismic fault zones
R309-515-4(7) | Location of each point of diversion provided (lat and long; or section, township, range)
N/A | Project will resolve existing physical deficiencies
General Requirements for UV
R309-520-8(1) | Ultraviolet light is used for inactivation of Crytosporidium, Giardia, and viruses
R309-520-8(1)(a) | For surface water or ground water under the influence of surface water, there is an additional means of disinfection
R309-520-8(1)(a) | For surface water or GWUDI, a min. of one alternative primary disinfectant is specified for virus inactivation
R309-520-8(1)(a) | For surface water or GWUDI, a secondary disinfectant is specified to maintain a distribution system disinfectant residual
R309-520-8(1)(b) | To receive credit for UV disinfection, R309-520-8(1)(b)(i) through (iv) below are met:
R309-520-8(1)(b)(i) | UV plan provided that identifies dose monitoring strategy (UV intensity set-point, calculated dose, or alternative approach)
R309-520-8(1)(b)(ii) | Goals are identified for UV facility as part of comprehensive disinfection strategy (target pathogens, target log inactivation, & corresponding required UV dose per Table 215-5 in R309-215-15(19)(d))
R309-520-8(1)(b)(iii) | UV reactor validation report per R309-520-8(2) submitted prior to installation of UV facility
R309-520-8(1)(b)(iv) | Demonstrate that reactor is delivering required UV dose using validated dose monitoring system
R309-520-8(1)(b)(iv) | Comply with monitoring and reporting requirements specified in R309-215-15(19) & (20)
Validation Testing for UV
R309-520-8(2) | Director has accepted validation based on 2003 UV Disinfection Guidance Manual (case by case)
R309-520-8(2)(a) | Each model and specific UV reactor configuration has undergone off-site, full-scale validation testing by an independent 3rd party test facility prior to approval for use
R309-520-8(2)(a) | Validation testing was done in qualified test facility accepted by NSF, EPA, or the Director
R309-520-8(2)(b) | Validation testing results provide data, including calculation & tables or graphical plots, of dose delivery by UV reactor under design conditions of flow rate, UV transmittance, UV intensity, lamp status, and power ballast setting and consider lamp aging and fouling
R309-520-8(2)(b) | Validation report demonstrates that monitoring algorithm is valid over expected range
R309-520-8(2)(b) | Validation testing data is used to define the dose monitoring algorithm for the UV reactor and operating conditions that can be monitored to ensure that required UV dose for a given pathogen inactivation credit is delivered
R309-520-8(2)(c) | UV reactor validation report includes R309-520-8(2)(c)(i) through (viii) below:
R309-520-8(2)(c)(i) | Report includes description of reactor and validation test set-up, including general arrangement and layout drawings of reactor and validation test piping arrangement
R309-520-8(2)(c)(ii) | Report includes description of methods used to empirically validate the reactor
R309-520-8(2)(c)(iii) | Report includes description of dose monitoring equation for reactor to achieve target pathogen inactivation credit and related graphical plots showing how the equation was derived from measured doses obtained through validation testing under varying test conditions
R309-520-8(2)(c)(iv) | Report includes range of validated conditions for flow, UVT, UV dose, and lamp status
R309-520-8(2)(c)(v) | Report includes description and rationale for selecting the challenge organism used in validation testing and analysis to define operating dose for pathogen inactivation credit
R309-520-8(2)(c)(vi) | Report includes tabulated data, analysis, and quality assurance/quality control measures used during validation testing
R309-520-8(2)(c)(vii) | Report includes licensed PE’s 3rd party oversight certification indicating that testing and data analyses in the validation report were conducted in a technically sound manner without bias
R309-520-8(2)(c)(viii) | Validation report includes completed Checklists 5.1 – 5.5 from EPA Ultraviolet Disinfection Guidance Manual for Final Long Term 2 Enhanced Surface Water Treatment Rule
Design Criteria for UV
R309-520-8(3)(a) | Sufficient water quality data gathered prior to design
R309-520-8(3)(a) | Water samples are representative of source water to be treated by UV facility
R309-520-8(3)(a) | Frequent testing done if significant variation or seasonal trending in water quality is expected
R309-520-8(3)(b)(i) – (x) | Following parameters considered in UV facility planning: UV Transmittance/UV Absorbance, Calcium, Alkalinity, Hardness, Iron, Manganese, Turbidity, pH, Oxidation-Reduction Potential, Particle Content, Algae
R309-520-8(3)(c) | Design flow rate and UVT were used to size UV system to provide required dose at min. of 95% of the time accounting for seasonal variations of flow and UVT combinations
R309-520-8(3)(c) | Matrix of flow and UVT conditions for UV reactors specified if necessary
R309-520-8(3)(d) | Delivered dose is beyond required UV dose in Table 215-5 (R309-215-15(19)(d)) to provide flexibility & conservatism (optional)
R309-520-8(3)(e) | UV reactor inlet and outlet configurations meet validated hydraulic distribution of flow or are more hydraulically conservative by following R309-520-8(3)(e)(i) or (ii) below:
R309-520-8(3)(e)(i) | Inlet and outlet configurations meet one of conditions specified in Section 3.6.2 of 2006 Final UVDGM
R309-520-8(3)(e)(ii) | Computational Fluid Dynamics-based modeling is used to demonstrate that given conditions of inlet and outlet piping with the UV installation provide equal or greater dose delivery; CFD modeling conducted at min. and max. values of validated range of flow, UVT, and lamp status
R309-520-8(3)(f) | UV disinfection system is capable of applying required design dose with a failed or out-of-service reactor
R309-520-8(3)(f) | Design accounts for on-line backup UV reactor or operating scheme to apply the design dose with one reactor out of service
R309-520-8(3)(g) | Each reactor can be isolated for maintenance
R309-520-8(3)(h) | Signals and alarms are provided for operation of UV facility for parameters necessary for dose monitoring algorithm (e.g., low UV dose, high flow rate, low UVT, UVT monitoring failure, UV sensor failure, off spec event, Ground Fault Interrupt, high water temp., low water level)
R309-520-8(3)(i) | All materials in UV reactors in contact with water meet ANSI/NSF 61
R309-520-8(3)(j) | Chemicals used to clean UV reactor components in contact with drinking water meet ANSI/NSF 60
R309-520-8(3)(k) | Flow or time delay is provided to allow sufficient time for tube warm-up per manufacturer’s recommendations before water flows from the unit upon start up
R309-520-8(3)(k) | Flow or time delay is included in design so excessive off-specification conditions do not result
R309-520-8(3)(l) | Backup power supply of sufficient capacity is provided for UV disinfection system
R309-520-8(3)(l) | If power quality problems anticipated, power conditioning equipment (e.g., uninterruptible power supply) is included in design
R309-520-8(3)(m) | Design includes redundant disinfection mechanism to apply approved primary disinfectant to achieve CT or log removal/inactivation required for compliance within a max. of 15 minutes when a UV facility is off spec or offline
R309-520-8(3)(n) | UV disinfection units rated at 30 gpm or less are certified to meet ANSI/NSF 55, Class A, or equivalent or more stringent validation or certification standards acceptable to the Director
R309-520-8(3)(o) | Dose monitoring approach for UV facility is consistent with 2006 Final UVDGM guidelines & accepted by the Director
R309-520-8(3)(p) | If PLC or SCADA interface is used for UV reactor’s process control, the programming is in accordance with validated dose monitoring algorithm and validated conditions
R309-520-8(3)(p) | Algorithm uses inputs of flow, UV intensity sensor readings, lamps status, and/or UVT equal to or more conservative than values measured during operation of UV system
R309-520-8(3)(p) | If measured UVT is above validated range, the max. validated UVT is used as the dose algorithm input
R309-520-8(3)(p) | If measured flow rate is below validated range, min. validated flow rate is used as the dose algorithm input
R309-520-8(3)(p) | If the dose algorithm uses relative lamp output determined from UV intensity sensor readings as an input, the relative lamp output is based on the measured UVT, even if it exceeds the max. validated UVT
R309-520-8(3)(q) | UV reactor’s PLC or microprocessor is programmed to record off-spec events for R309-520-8(3)(q)(i) through (v) below:
R309-520-8(3)(q)(i) | Delivered UV dose is less than the required dose
R309-520-8(3)(q)(ii) | Flow is greater than the validated range
R309-520-8(3)(q)(iii) | UVT is less than the validated range
R309-520-8(3)(q)(iv) | Lamp status is outside the validated range
R309-520-8(3)(q)(v) | Failure of UV sensors, flow meters, or online UVT monitors is used in the dose calculation
Operation and Maintenance
R309-520-8(4) | Approved UV installations follow manufacturer’s recommendations or guidelines in Sections 6.2 through 6.5 of 2006 Final UVDGM for operation and maintenance
Start-up Testing
R309-520-8(4)(a)(i) | UV reactor manufacturer provided site-specific O&M manual that includes start-up and shut-down procedures for UV treatment system
R309-520-8(4)(a)(ii) | Schedules and performance standards for start-up testing and initial operation are provided
R309-520-8(4)(a)(ii) | Schedules include anticipated start-up date and proposed testing duration
R309-520-8(4)(a)(ii) | Performance standards reference applicable regulations and specific equipment capabilities
R309-520-8(4)(a)(iii) | Operators receive site-specific training on operation of UV disinfection system
R309-520-8(4)(b) | Incident plan developed to address lamp breakage and mercury release, response to alarms, power supply interruptions, activation of standby equipment, failure of system, etc.
R309-520-8(4)(c) | Selected parameters are monitored to verify that UV reactors are operated within validated limits
R309-520-8(4)(c) | Routine O&M includes monitoring and calibration requirements in R309-215-15(19) & (20) and according with O&M protocol approved by the Director
R309-520-8(4)(c) | For very small UV systems, Director has granted exception that allows reduced monitoring and reporting (case by case)