## Fluoridation Facility Checklist
Fluoridation Facility |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by a Utah PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs (if applicable)
R309-500-10 | Method of wastewater disposal approved by DWQ or LHD (new water facilities/proposed developments) (if applicable)
R309-400 | Project will resolve existing physical deficiencies
All Fluoridation Facilities - Chemicals and Materials
R309-535-5(2)(a)(i) | Chemicals certified to meet ANSI/NSF 60
R309-535-5(2)(a)(ii) | Fluoridation equipment materials compatible with fluoridation chemicals
R309-535-5(2)(a)(iii) | Fluoridation equipment metal parts corrosion resistant
R309-535-5(2)(a)(iv) | Lead weights absent in fluoride chemical solution day and bulk tanks
All Fluoridation Facilities- Chemical Storage
R309-535-5(2)(b)(i) | Fluoride chemicals stored in covered or sealed containers [OPERATIONAL]
R309-535-5(2)(b)(i) | Fluoride chemicals stored in a building
R309-535-5(2)(b)(i) | Fluoride chemicals stored away from direct sunlight
R309-535-5(2)(b)(i) | Fluoride chemicals stored away from heat source
R309-535-5(2)(b)(ii) | Fluoride chemicals stored separate from incompatible chemicals [OPERATIONAL]
R309-535-5(2)(b)(iii) | Containers for dry materials kept closed [OPERATIONAL]
R309-535-5(2)(b)(iv) | Fluoride solution tanks labeled to identify contents
All Fluoridation Facilities - Secondary Containment
R309-535-5(2)(c)(i) | Fluoride solution tanks provided with secondary containment
R309-535-5(2)(c)(ii) | Secondary containment sized to contain maximum volume of solution handled
R309-535-5(2)(c)(iii) | Secondary containment acid resistant
All Fluoridation Facilities- Means to Measure
R309-535-5(2)(d)(i) | Means to measure treated water provided
R309-535-5(2)(d)(ii) | Means to measure level in solution tank provided
R309-535-5(2)(d)(ii) | Means to measure quantity of chemicals used provided
R309-535-5(2)(d)(iii) | Sampling point to measure fluoride level of treated water provided downstream of fluoridation facility
All Fluoridation Facilities- Fluoride Feed Pump
R309-535-5(2)(e)(i) | Fluoride feed pump sized to prevent fluoride overfeed
R309-535-5(2)(e)(i) | Fluoride feed pump sized to consider operational efficiency
R309-535-5(2)(e)(ii) | Fluoride feed pump provided with anti-siphon device
R309-535-5(2)(f) | Electrical outlet for feed pump has interlock protection (wired to well or service pump)
R309-535-5(2)(f) | Fluoride feed pump not plugged into continuously active electrical outlet
All Fluoridation Facilities- Fluoride Injection
R309-535-5(2)(g)(i) | Fluoride injection line enters at lower third of water line
R309-535-5(2)(g)(i) | End of injection line located in lower half of water line
R309-535-5(2)(g)(ii) | Fluoride injection point allows adequate mixing
R309-535-5(2)(g)(iii) | Fluoride injection point downstream of lime softening, ion exchange, or other fluoride-affecting processes
R309-535-5(2)(g)(iv) | Fluoride injector adequate for quantity of fluoride to be added
R309-535-5(2)(g)(iv) | Fluoride injector adequate for water flow
R309-535-5(2)(g)(iv) | Fluoride injector adequate for back pressure
R309-535-5(2)(g)(iv) | Fluoride injector adequate for injector operating pressure
R309-535-5(2)(g)(v) | Corporation stop provided at injection point for fluoride injected under pressure
R309-535-5(2)(g)(vi) | Anti-siphon device provided at fluoride injection point
All Fluoridation Facilities- Minimize Fluoride Overfeed
R309-535-5(2)(h)(i) | In addition to feed pump control, a secondary control mechanism is provided to minimize fluoride overfeed
R309-535-5(2)(h)(ii) | For facilities without on-site operators, a day tank or two alternative secondary controls provided
All Fluoridation Facilities- Housing
R309-535-5(2)(i) | Building housing fluoridation equipment designed to be secure
R309-535-5(2)(i) | Building housing fluoridation equipment adequately sized to handle and store fluoride chemicals
All Fluoridation Facilities- Heating, Lighting, and Ventilation
R309-535-5(2)(j)(i) | Building designed with adequate heating, lighting, and ventilation for proper operation of equipment
R309-535-5(2)(j)(i) | Building designed with adequate heating, lighting, and ventilation for operator safety
R309-535-5(2)(j)(ii) | Ventilation in fluoride operating area designed to provide min. of six complete room-air changes per hour
R309-535-5(2)(j)(iii) | Fluoride operating area vented to outside
R309-535-5(2)(j)(iii) | Fluoride operating area vented away from air intakes
R309-535-5(2)(j)(iv) | Separate switches provided for fluoride operating area fans and lights
R309-535-5(2)(j)(iv) | Switches for fans and lights located outside of, or near, entrance to fluoride operating area
R309-535-5(2)(j)(iv) | Switches for fans and lights protected from vandalism
All Fluoridation Facilities- Cross Connection Control
R309-535-5(2)(k) | Cross connection control provided by air gap or approved backflow prevention assembly
Fluorosilicic Acid Installations
R309-535-5(3)(a) | Fluorosilicic acid to be injected without prior manual, on-site dilution [OPERATIONAL]
R309-535-5(3)(e) | Neutralizing chemical provided on site to handle small-quantity acid spills
Fluorosilicic Acid Installations - Solution Tank Vents
R309-535-5(3)(b)(i) | Bulk tank provided with vent
R309-535-5(3)(b)(ii) | Tanks vented to outside
R309-535-5(3)(b)(ii) | Tank venting terminates above grade
R309-535-5(3)(b)(ii) | Tanks vented away from air intakes
R309-535-5(3)(b)(ii) | Tanks vented where least susceptible to contamination (precipitation, dust, etc.)
R309-535-5(3)(b)(iii) | Bulk tank and day tank have separate vents if risk of overflow from bulk to day tank exists
R309-535-5(3)(b)(iv) | Discharge end of vent screened with non-corrodible No. 14 or finer mesh
Fluorosilicic Acid Installations - Built Only after January 1, 2017
R309-535-5(3)(c) | A view window provided between control room and operating area if separate rooms are provided
Fluorosilicic Acid Installations - Emergency Facilities
R309-535-5(3)(d) | Emergency eyewash station provided
R309-535-5(3)(d) | Emergency shower provided
Fluorosilicic Acid Installations - Personal Protective Equipment
R309-5353-5(3)(f)(i) | Full-face shield and splash-proof safety goggles provided
R309-5353-5(3)(f)(ii) | Long gauntlet acid-resistant rubber or neoprene gloves with cuffs provided
R309-5353-5(3)(f)(iii) | Acid-resistant rubber or neoprene aprons provided
R309-5353-5(3)(f)(iv) | Rubber boots provided
Fluoride Saturator Installations - Equipment
R309-535-5(4)(a) | Water meter provided on make-up water line
R309-535-5(4)(b) | Min. depth of fluoride chemical required to maintain saturated solution marked on outside of saturator tank [OPERATIONAL]
R309-535-5(4)(c) | Saturator operated so that undissolved chemical is not drawn into suction line [OPERATIONAL]
R309-535-5(4)(d) | Make-up water supply line terminates a min. of two pipe diameters above solution tank or has backflow protection
Fluoride Saturator Installations - Make-up Water Softening
R309-535-5(4)(e)(i) | Make-up water with hardness above 75 mg/L is softened
R309-535-5(4)(e)(ii) | 20-mesh sediment filter is installed on saturator make-up water line between softener and water meter
Fluoride Saturator Installations - Dust Control
R309-535-5(4)(f) | Fluoride dust minimized during transfer of dry compounds [OPERATIONAL]
R309-535-5(4)(f) | Fluoride dust minimized during disposal of bags, drums, or barrels [OPERATIONAL]
R309-535-5(4)(f) | Fluoride dust minimized during cleaning [OPERATIONAL]
Fluoride Saturator Installations - Emergency Eyewash
R309-535-5(4)(g) | Emergency eyewash provided
Fluoride Saturator Installations - Personal Protective Equipment
R309-535-5(4)(h)(i) | NIOSH-approved particulate respirator with soft rubber face-to-mask seal and replaceable cartridges provided
R309-535-5(4)(h)(ii) | Chemical dust-resistant safety goggles provided
R309-535-5(4)(h)(iii) | Acid-resistant gloves provided
R309-535-5(4)(h)(iv) | Acid-resistant rubber or neoprene aprons provided
R309-535-5(4)(h)(v) | Rubber boots provided
Fluoride Dry Feed Installations - Equipment
R309-535-5(5)(a) | Solution tank provided for volumetric and gravimetric dry feeders
R309-535-5(5)(b) | Mechanical mixer provided in solution tank
Fluoride Dry Feed Installations - Dust Control
R309-535-5(5)(c)(i) | Fluoride dust minimized during transfer of dry compounds [OPERATIONAL]
R309-535-5(5)(c)(i) | Fluoride dust minimized during disposal of bags, drums, or barrels [OPERATIONAL]
R309-535-5(5)(c)(i) | Fluoride dust minimized during cleaning [OPERATIONAL]
R309-535-5(5)(c)(ii) | Hopper, if present, is equipped with dust filter and exhaust fan that places it under negative pressure
R309-535-5(5)(c)(iii) | Air from fluoride handling equipment discharges through a dust filter to atmosphere outside of building
Fluoride Dry Feed Installations - Emergency Eyewash
R309-535-5(5)(d) | Emergency eyewash provided
Fluoride Dry Feed Installations - Personal Protective Equipment
R309-535-5(5)(e)(i) | NIOSH-approved particulate respirator with soft rubber face-to-mask seal and replaceable cartridges provided
R309-535-5(5)(e)(ii) | Chemical dust-resistant safety goggles provided
R309-535-5(5)(e)(iii) | Acid-resistant gloves provided
R309-535-5(5)(e)(iv) | Acid-resistant rubber or neoprene aprons provided
R309-535-5(5)(e)(v) | Rubber boots provided