## Misc Treatment Checklist
Miscellaneous Treatment Methods |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information |  | Professional Engineer Responsible for Design
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
DDW Plan Review Information
Project File Number:
Plan Review Engineer:
Instructions: In the appropriate column below, for the Design Engineer or DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
|  |  |  | Engineer | (note reason below if answer is 'No')
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Exception to rule requirements granted by the Director for alternative designs
R309-535-4 | Plans and specs for specialized treatment incorporate requirements from relevant sections of other drinking water engineering rules for the specified treatment method and, where applicable, include (1) through (9) below:
R309-535-4(1) | Plant Siting (see R309-525-6)
R309-535-4(2) | Plant Reliability (see R309-525-7)
R309-535-4(3) | Color Coding and Pipe Marking (see R309-525-8)
R309-535-4(4) | Chemical Addition (see R309-525-11)
R309-535-4(5) | Miscellaneous Plant Facilities (see R309-525-17, particularly sub-section R309-525-17(1), Laboratory)
R309-535-4(6) | Operation and Maintenance Manuals (see R309-525-19)
R309-535-4(7) | Safety (see R309-525-21)
R309-535-4(8) | Disposal of Treatment Plant Waste (see R309-525-23)
R309-535-4(9) | Disinfection (see R309-520)
N/A | Project will resolve existing physical deficiencies
Taste and Odor Control
R309-535-6 | Design and operation of taste and odor control facilities complies with Part 4, Section 4.9, Taste and Odor Control, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Stabilization
R309-535-7 | Design and operation of stabilization facilities complies with Part 4, Section 4.8, Stabilization, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Deionization
R309-535-8 | Current practical methods of deionization include Ion Exchange, Reverse Osmosis, and Electrodialysis (informational)
R309-535-8 | Additional methods of deionization may be approved subject to the presentation of evidence of satisfactory reliability (informational)
R309-535-8 | The groundwater source exceeds 2,000 mg/L Total Dissolved Solids or 500 mg/L Sulfate, is not diluted, and will be treated by the methods outlined in this section
R309-535-8 | Deionization cannot be considered a substitute process for conventional complete treatment outlined in R309-525 (informational)
Ion Exchange - General
R309-535-8(1)(a) | Loading the media with water high in organics is avoided
Ion Exchange - Design
R309-535-8(1)(b)(i) | Pretreatment is provided per the manufacturer's recommendation
R309-535-8(1)(b)(ii) | Upflow or downflow units are used
R309-535-8(1)(b)(iii) | Exchangers have at least a three foot media depth
R309-535-8(1)(b)(iv) | Exchangers are designed to meet the recommendations of the media manufacturer with regard to flow rate or contact time
R309-535-8(1)(b)(iv) | Flow is ≤7 gpm/sf of bed area
R309-535-8(1)(b)(iv) | The plant is provided with an influent or effluent meter
R309-535-8(1)(b)(iv) | The plant is provided with a meter on any bypass line
R309-535-8(1)(b)(v) | Chemical feeders conform to R309-525-8
R309-535-8(1)(b)(v) | All solution tanks are covered
R309-535-8(1)(b)(vi) | Regenerants added are uniformly distributed over the entire media surface of upflow or downflow units
R309-535-8(1)(b)(vi) | Regeneration is done according to the media manufacturer's recommendations
R309-535-8(1)(b)(vii) | The wash rate capability is in excess of the manufacturer's recommendation
R309-535-8(1)(b)(vii) | The wash rate capability is at least 6 to 8 gpm/sf of bed area
R309-535-8(1)(b)(viii) | Disinfection (see R309-520) is provided ahead of the exchange units and does not interfere with the media
R309-535-8(1)(b)(viii) | Disinfection is after the treatment process because it interferes with the media
Reverse Osmosis - General
R309-535-8(2)(a) | The design permits the easy exchange of modules for cleaning or replacement
Reverse Osmosis - Design Criteria
R309-535-8(2)(b)(i) | Pretreatment is provided per the manufacturer's recommendation
R309-535-8(2)(b)(ii) | Pressure gauges are provided on the upstream and downstream side of the filter
R309-535-8(2)(b)(ii) | A conductivity meter is present at the site
R309-535-8(2)(b)(ii) | Taps are provided for sampling permeate
R309-535-8(2)(b)(ii) | Taps are provided for sampling concentrate
R309-535-8(2)(b)(ii) | Taps are provided for blended flows
R309-535-8(2)(b)(ii) | If a continuous conductivity meter is permanently installed, piping is such that the meter can be disconnected and calibrated with standard solutions at a frequency recommended by the manufacturer
R309-535-8(2)(b)(iii) | Aeration, if practiced, conforms with provisions of R309-535-9
R309-535-8(2)(b)(iv) | Cleaning is routinely done in accordance with the manufacturer's recommendations
R309-535-8(2)(b)(v) | Where the feed water pH is altered, the finished water is stabilized
Reverse Osmosis - Waste Disposal
R309-535-8(2)(c) | Waste generated by reverse osmosis treatment is disposed of in accordance with R309-525-23
Electrodialysis - Design
R309-535-8(3)(b)(i) | Pretreatment is provided per the manufacturer’s recommendation
R309-535-8(3)(b)(ii) | Design includes the ability to measure plant flow rates
R309-535-8(3)(b)(ii) | Design includes the ability to measure feed temperature if water is heated
R309-535-8(3)(b)(ii) | Design includes a high temperature automatic cutoff to prevent membrane damage if water is heated
R309-535-8(3)(b)(ii) | Design includes the ability to measure D.C voltage at the first and second stages as well as on each of the stacks
R309-535-8(3)(b)(ii) | Sampling taps are provided to measure the conductivity of the feed water
R309-535-8(3)(b)(ii) | Sampling taps are provided to measure the conductivity of the blowdown water
R309-535-8(3)(b)(ii) | Sampling taps are provided to measure the conductivity of the product water
R309-535-8(3)(b)(ii) | D.C. and A.C. kilowatt-hour meters to record the electricity used are provided
Electrodialysis - Waste Disposal
R309-535-8(3)(c) | Waste generated by electrodialysis treatment is disposed of in accordance with R309-525-23
Aeration
R309-535-9 | Design and operation of aeration facilities complies with Part 4, Section 4.5, Aeration, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Softening
R309-535-10 | Design and operation of softening facilities complies with Part 4, Section 4.4, Softening, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Iron and Manganese Control
R309-535-11 | The iron & manganese control treatment process used will depend on the character of the source water (informational)
R309-535-11 | The iron and manganese treatment processes meet specific local conditions as determined by engineering investigations, including chemical analyses of representative samples of water to be treated, and have been approved by the Director
R309-535-11 | It may be necessary to operate a pilot plant in order to gather all information pertinent to the design (informational)
R309-535-11 | pH adjustment of the raw water to increase the rate of the chemical reactions involved was considered
Removal by Oxidation, Detention, and Filtration - Oxidation
R309-535-11(1)(a) | Oxidation may be by aeration, or by chemical oxidation with chlorine, potassium permanganate, ozone, or chlorine dioxide (informational)
Removal by Oxidation, Detention, and Filtration - Oxidation - Detention - Reaction Time
R309-535-11(1)(b)(i) | A minimum detention time of 20 minutes is provided following aeration to ensure that the oxidation reactions are as complete as possible
R309-535-11(1)(b)(i) | The minimum detention time of 20 minutes is omitted because a pilot plant study indicates no need for detention
R309-535-11(1)(b)(i) | The detention basin is designed as a holding tank with no provisions for sludge collection
R309-535-11(1)(b)(i) | The detention basin is designed with sufficient baffling to prevent short circuiting
Removal by Oxidation, Detention, and Filtration - Oxidation - Detention - Sedimentation
R309-535-11(1)(b)(ii) | Sedimentation basins are provided when treating water with high iron and/or manganese content or where chemical coagulation is used to reduce the load on the filters
R309-535-11(1)(b)(ii) | Sludge removal is provided
Removal by Oxidation, Detention, and Filtration - Filtration - General
R309-535-11(1)(c)(i) | The number of pressure filters is at least equal to the number of rapid-rate gravity filters
R309-535-11(1)(c)(i) | The structural details for pressure filters are at least equal to the criteria for rapid-rate gravity filters
R309-535-11(1)(c)(i) | The hydraulics for pressure filters is at least equal to the criteria for rapid-rate gravity filters
R309-535-11(1)(c)(i) | The media for pressure filters are at least equal to the criteria for rapid rate gravity filters
R309-535-11(1)(c)(i) | Although the minimum criteria provided for rapid rate gravity filters apply to pressure filters where appropriate and may be used in this application, they cannot be used in the filtration of surface waters or following lime-soda softening (informational)
Removal by Oxidation, Detention, and Filtration - Filtration - Design Details for Pressure Filter
R309-535-11(1)(c)(ii) | Pressure filters meet requirements (A) through (J) below:
R309-535-11(1)(c)(ii)(A) | Loss of head gauges on the inlet and outlet pipes of each filter
R309-535-11(1)(c)(ii)(B) | An easily readable meter or flow indicator on each battery of filters
R309-535-11(1)(c)(ii)(C) | Filtration and backwashing of each filter individually with an arrangement of piping as simple as possible to accomplish these purposes
R309-535-11(1)(c)(ii)(D) | Top of the washwater collectors are at least twenty-four (24) inches above the surface of the media
R309-535-11(1)(c)(ii)(E) | An underdrain system to efficiently collect the filtered water and to uniformly distribute the backwash water at a rate capable of not less than 15 gpm/sf of filter area
R309-535-11(1)(c)(ii)(F) | Backwash flow indicators and controls that are easily readable while operating the control valves
R309-535-11(1)(c)(ii)(G) | An air release valve on the highest point of each filter
R309-535-11(1)(c)(ii)(H) | An accessible manhole to facilitate inspections and repairs
R309-535-11(1)(c)(ii)(I) | Means to observe the wastewater and filters during backwashing
R309-535-11(1)(c)(ii)(J) | Cross-connections prevented
Removal by Lime-Soda Softening Process
R309-535-11(2) | Design and operation of the lime-soda softening process complies with Part 4, Section 4.4, Softening, in the Recommended Standards for Water Works (commonly known as "Ten State Standards"), 2007 edition, published by the Great Lakes-Upper Mississippi River Board of Public Health and Environmental Managers
Removal by Manganese Greensand Filtration
R309-535-11(3) | This process, consisting of the continuous feed of potassium permanganate to the influent of a manganese greensand filter, is more applicable to the removal of manganese than the removal of iron (informational)
R309-535-11(3)(a) | Permanganate is applied as far ahead of the filter as practical and at a point immediately before the filter
R309-535-11(3)(b) | An anthracite media cap of at least six inches is provided over manganese greensand
R309-535-11(3)(c) | The normal filtration rate is 3 gpm/sf
R309-535-11(3)(d) | The normal wash rate is 8 to 10 gpm/sf
R309-535-11(3)(e) | Air washing is provided
R309-535-11(3)(f) | Sample taps are provided as indicated in (i) through (v) below:
R309-535-11(3)(f)(i) | Located before application of permanganate
R309-535-11(3)(f)(ii) | Located immediately ahead of filtration
R309-535-11(3)(f)(iii) | Located between the anthracite media and the manganese greensand
R309-535-11(3)(f)(iv) | Located halfway down the manganese greensand
R309-535-11(3)(f)(v) | Located at the filter effluent
Removal by Ion Exchange
R309-535-11(4) | This process is not acceptable where either the source water or wash water contains dissolved oxygen (informational)
Sequestration by Polyphosphates
R309-535-11(5) | The iron, manganese, or total of them is ≤1.0 milligram per liter when this process is proposed
R309-535-11(5) | The total phosphate applied is ≤10 milligrams per liter as PO4
R309-535-11(5) | Where phosphate treatment is used, satisfactory chlorine residuals are maintained in the distribution system and requirements (a) through (d) below are met:
R309-535-11(5)(a) | Feeding equipment conforms to the requirements of R309-525-11(7)
R309-535-11(5)(b) | Stock phosphate solution is kept covered and disinfected by carrying approximately 10 mg/l free chlorine residual
R309-535-11(5)(c) | Application of polyphosphates is avoided before iron and manganese removal treatment
R309-535-11(5)(c) | Where no iron or manganese removal treatment is provided, the point of application is prior to any aeration, oxidation, or disinfection steps
R309-535-11(5)(d) | Phosphate chemicals comply with ANSI/NSF Standard 60
R309-535-11(5)(d) | Sampling taps are provided for control purposes
R309-535-11(5)(d) | Sampling taps are located on each raw water source
R309-535-11(5)(d) | Sampling taps are located on each treatment unit influent
R309-535-11(5)(d) | Sampling taps are located on each treatment unit effluent
R309-535-11(5)(d) | Waste generated by iron and manganese control treatment is disposed of in accordance with R309-525-23
Point-of-Use and Point-of-Entry Treatment Devices
R309-535-12 | Drinking water does not meet the quality standards of R309-200, available water system treatment methods have been determined to be unreasonably costly or otherwise undesirable, and the Director has approved the installation and maintenance of point-of-use devices
R309-535-12 | Drinking water does not meet the quality standards of R309-200, available water system treatment methods have been determined to be unreasonably costly or otherwise undesirable, and the Director has approved the installation and maintenance of point-of-entry treatment devices
R309-535-12 | The Director has received and approved items (1) through (8) below:
R309-535-12(1) | An analysis in the form of an engineering report that clearly demonstrates that central treatment is not feasible for the public water system
R309-535-12(1) | The analysis is prepared by a professional engineer registered in Utah (unless the system serves <75 connections)
R309-535-12(1) | The analysis is not prepared by a professional engineer because the system serves <75 connections
R309-535-12(2) | The water system has a signed access agreement with each customer that allows water system personnel to enter their property on a scheduled basis to install and maintain the treatment devices
R309-535-12(2) | The agreement includes educational information with regard to the health risks of consuming or cooking with water from non-treated taps
R309-535-12(2) | Systems with an initial 75% of their connections under a signed access agreement will be allowed to proceed with the understanding that 100% of their connections are due within a 5 year period (informational)
R309-535-12(2) | Signed access agreements are not provided for customers because the public water system owns or controls all connections to the public water system
R309-535-12(3) | Documentation that legal authority, which includes a termination of service clause, has been adopted to ensure water system access to the property for installation, maintenance, servicing and sampling of each treatment unit
R309-535-12(3) | Documentation of legal authority for access to property to install, maintain, service, and sample each treatment unit is not provided because the public water system owns or controls all connections to the public water system
R309-535-12(4) | Point-of-use or point-of-entry treatment devices are proven to be appropriate, safe and effective as determined through testing and compliance with protocols established by EPA's Environmental Technology Verification Program (ETV) or the applicable ANSI/NSF Standard(s)
R309-535-12(4) | A pilot study was required by DDW to determine the suitability of the point-of-use or point-of-entry device in treating a particular source water
R309-535-12(4) | The scope and duration of the pilot study was determined by such factors as the characteristics of the raw water, manufacturer's ratings of the treatment device, and good engineering practices
R309-535-12(4) | The pilot study generated data on service intervals, aid in specifying and calibrating alarm systems, and revealed site specific problems with component fouling or microbial colonization
R309-535-12(5) | An operation and maintenance plan to be implemented by the public water system is provided demonstrating that the treatment units will be installed and serviced according to the manufacturer's instructions and that compliance sampling as required in R309-215-6 will take place
R309-535-12(5) | The public water system will provide documentation of an operation and maintenance contract or schedule annually as required in R309-105-16(4)
R309-535-12(5) | If the O&M of the POU/POE devices is performed by water system personnel, it will be performed by a water operator certified at the level of the water system
R309-535-12(6) | The performance indicating device for the point-of-use/point-of-entry treatment device that will be used is specified in the submittal for plan approval
R309-535-12(7) | A customer education and out-reach plan to be implemented by the public water system that includes at a minimum annual frequency of contact is provided
R309-535-12(8) | Point-of-use or point-of-entry treatment devices for compliance with the nitrate MCL will be provided at all taps that are accessible to the public
New Treatment Processes or Equipment
R309-535-13 | The policy of the Board is to encourage, rather than to obstruct, the development of new methods and equipment for the treatment of water (informational)
R309-535-13 | The New process or new equipment has been thoroughly tested in full-scale, comparable installations before plans have been submitted for review and approval
R309-535-13 | The U.S. Environmental Protection Agency (EPA) has created the Environmental Technology Verification (ETV) Program to facilitate the deployment of innovative or improved environmental technologies through performance verification and dissemination of information (informational)
R309-535-13 | NSF International (NSF) in cooperation with the EPA operates the Package Drinking Water Treatment Systems (PDWTS) pilot, one of 12 technology areas under ETV; Engineers and Manufacturers are referred to Manager, ETV project, NSF International, P.O. Box 130140, Ann Arbor, Michigan 48113-0140 (informational)
R309-535-13 | The designer or supplier has presented evidence satisfactory to the Director that the new treatment process will insure the delivery of safe, sanitary water without imposing undue problems of supervision, operation, or control