## Sheet1
Estimate Disinfection CT & Whether Meeting 4-Log Virus Inactivation | [6 empty] | Enter only the green field
XYZ Water System |  |  |  | Water System # |  |  | File #
Estimate Pipe Volume |  |  |  | V=L*Pi*(R)2
Pipe Description | Length (ft) | Diameter (inches) | Diameter (feet) | Volume (ft3) | Volume (gal) | % Full | Effective Water Volume (gal)
Transmission 1 | 800 | 24 | 2 | 2513.2741 | 18799.2901 | 100% | 18799.2901
T 2 | 100 | 18 | 1.5 | 176.7146 | 1321.8251 | 50% | 660.9125
|  |  | 0 | 0 | 0 |  | 0
|  |  | 0 | 0 | 0 |  | 0
|  |  | 0 | 0 | 0 |  | 0
|  |  | 0 | 0 | 0 |  | 0
|  |  | 0 | 0 | 0 |  | 0
|  |  |  | Total Pipe Effecive Volume (gallons) |  |  | 19460.2027
Estimate Pipe Disinfection CT
Residual Conc., C (mg/L) 1 | pH 2 | Temp. (°C) 3 (See Table B below) | Peak Flow (gpm) | Effective Volume (gal) | Total Detention Time (min) | Contact Time (T) (min) | Total Pipe CT (C*T) 4
0.3 | 6-9 | 0.5 | 1000 | 19460.2027 | 19.4602 | 19.4602 | 5.8381
Estimate Storage Tank Volume & Disinfection CT
Tank Description | Residual Conc., C (mg/L) | pH 2 | Temp. (°C) 3 (See Table B below) | Peak Flow (gpm) | Baffling Factor, BF (See Table A below) | Minimum Volume (gal) (at lowest setting) | Total Detention Time, TDT (min) | Contact Time (T) (min) | CT (C*T)
[7 empty] | Vol/Peak Flow | TDT x BF | C*T
ST003 Tank | 0.3 | 6-9 | 0.5 | 3000 | 0.1 | 500000 | 166.6667 | 16.6667 | 5
|  | 6-9 | 0.5 | 1 |  |  | 0 | 0 | 0
|  | 6-9 | 0.5 | 1 |  |  | 0 | 0 | 0
|  | 6-9 | 0.5 | 1 |  |  | 0 | 0 | 0
|  | 6-9 | 0.5 | 1 |  |  | 0 | 0 | 0
|  | 6-9 | 0.5 | 1 |  |  | 0 | 0 | 0
[7 empty] | Total Tank CT 4 |  | 5
Summary
CT Req'd for 4-Log Virus Inactivation |  |  | 12 | (See Table B below, assuming worst scenario)
Total Estimated Disinfection CT 4 |  |  | 10.8381 | (= Total Pipe CT + Total Tank CT)
Meeting 4-Log Virus Inactivation? |  |  | No
Notes:
1. Residual conc. is the disinfectant level measured at (or after) the end of the pipe/vessel [NOT the dose added at the beginning of the pipe/vessel].
2. Assuming pH between 6 and 9
3. Assuming water temperature of 0.5 °C in winter worst scenario
4. This tool provides rough estimate of disinfection CT. For detailed design, apply additional safety factor and other design considerations.
| Table A |  |  |  |  | Table B
| Tank Baffling Factors |  |  |  |  | Free Chlorine CT Values (per EPA, 1991)
| Factor | Description |  |  |  | 4- Log Inactivation of Viruses
| 0.1 | None, agitated basin, very low length to width ratio, high inlet/outlet velocities |  |  |  | Temp (oC) | pH
[7 empty] | 6-9 | 10
| 0.3 | Single or mutliple unbaffled inlets or outlets, no intra-basin baffles |  |  |  | 0.5 | 12 | 90
[6 empty] | 5 | 8 | 60
| 0.5 | Baffled inlet/outlet with some intra-basin baffling |  |  |  | 10 | 6 | 45
[6 empty] | 15 | 4 | 30
| 0.7 | Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated launders |  |  |  | 20 | 3 | 22
[6 empty] | 25 | 2 | 15
| 1 | Very high L to W ratio (pipeline flow), perforated inlet, outlet & intra-basin baffles