## Sheet1
Energy (Cost Savings) Tracking Program
Date | Name of Water System | Water System Contact Information | Energy Efficient Project Description | Total Source Capacity in gpm | Annual Energy Cost Savings
2014-12-31 | Centerville City | Randy Randall rrandall@centervilleut.com 801-292-8232 | Find and repair leaks. Investigate and use optimal power rate schedules. Use smaller capacity pumps during off peak hours and run them for longer periods of time to save in monthly demand charges. Run pumps only on weekends to meet weekly demands. | 4000 | 252157 | OK
| Eagle Mountain | David Norman dnorman@emcity.org 801-789-6678 |  | 14634
2015-07-01 | Jordan Valley Water Conservancy District | Todd Schultz todds@jvwcd.org (801) 565-4359 | Developed culture of energy savings, from office staff to water operators to senior management. Determined energy cost of each water source or facility and adopted policy to use low-cost water first. Maintained pressure to deliver irrigation water without pumping. Used Echo Reservoir storage right for gravity-fed supply rather than pumping groundwater. | 140450 |  | Saved 2.8 million kWh from November 2014 to June 2015. That's a lot. Waiting for external report and verification from JVWCD (scheduled for August).
2014-06-01 | Logan City Water | Paul Lindhardt paul.lindhardt@loganutah.org 435-716-9622 | Create new pressure zone (split the City into two major pressure zones). Pump water to where it is mostly used at lower pumping head. | 27250 | 119791 | Actual savings in 2014. Updated from $119,791 projection.
2013-12-31 | Mountain Regional Water | Doug Evans doug@mtregional.org 435-940-1916 | Pump during off-peak periods. Run pumps at a slower and steady rate for a longer period. Avoid re-pumping. Implement a regular water loss audit and repair program. Ensure all large pumping facilities have PF correction devices using capacitors either directly or as part of a Variable Frequency Drives (VFD) system. | 33000 | 300000 | OK
2015-06-01 | North Salt Lake | Jonathan Rueckert jonr@nslcity.org 801-335-8700 | Adjusted valve settings to avoid redundant pumping. Developed awareness of energy requirements to avoid peak charges. Maximized storage use to meet peak demand with tanks instead of sources. | 7656 | 66000
| Park City | Clint McAffee clint.mcaffee@parkcity.org 435-615-5339 |  | 32382
2013-12-31 | Riverton City Water | Scott Hill shill@rivertoncity.com 801-254-0704 ext 103 | Replace old pumps with more efficient pumps at a pump station. | 32565 | 42110
2015-06-01 | Spanish Fork | Chris Thompson cthompson@spanishfork.org 801-804-4556 | Installed new pipeline to preserve pressure from mountain spring. Delivers water without pumping. | 23575 | 77000
2007-11-09 | Washington County Water Conservancy District | Hank Childers hchilders@wcwcd.utah.gov 435-673-3617 | Implementing batch production, shutting off the pretreatment blowers, and programming VFD and soft start pumps at their Qual Creek Water Treatment Plant | 33300 | 50000