## Capacity Calculations
Division of Drinking Water Water System Capacity Calculation Sheet (revised June 23, 2011)
Enter the green cells only.
System Name: |  | Fable Haven Town |  |  |  |  | System Number: | 11111
1. Indoor Water Use
| Number of residential connections |  |  | - - - - - - - - - - - | - - - - - - - - - - | - - - - - - - - - | - - - - - - - - - | 600
| Number of other connections - - - |  |  | 3 |  |  | ERCs of other connections | 75 | (Example: water use of 2 factory is equivalent to 30 homes.)
[7 empty] | Total Equivalent Residential Connections (ERCs) | 675
MINIMUM REQUIREMENTS FOR INDOOR WATER USE
| Source |  | Storage |  | Water Rights
| Per ERC | Total | Per ERC | Total | Per ERC | Total
| (gpd/ERC) | (gpm) | (gallons/ERC) | (gallons) | (ac-ft/yr) | (ac-ft/yr)
| 800 | 375 | 400 | 270000 | 0.45 | 303.75
2. Outdoor Water Use
Is the drinking water used for outdoor irrigation?
| Residential ERCs using drinking water for irrigation |  |  |  |  | - - - - - - - - - | - - - > > > | 360
| Percentage of Residential ERCs using DW for irrigation |  |  |  |  | - - - - - - - - - | - - - > > > | 60% | Map Zones
| Average irrigated acreage per residential connection |  |  |  |  | - - - - - - - - - | - - - > > > | 0.05 | 1
| Total irrigated acreage of other connections. |  |  |  |  | - - - - - - - - - | - - - > > > | 35 | 2
(Enter notes here. Check whether and what % of outdoor irrigation is supplied by drinking water.) | [6 empty] | Irrigation zone | 3 | 3
4
5
| MINIMUM REQUIREMENTS FOR OUTDOOR WATER USE | [7 empty] | 6
| Source |  | Storage |  | Water Rights
| Per ERC | Total | Per ERC | Total | Per ERC | Total
| (gpd/ERC) | (gpm) | (gallons/ERC) | (gallons) | (ac-ft/yr) | (ac-ft/yr)
| 244.08 | 179.67 | 126.4 | 133984 | 0.083 | 87.98
3. Fire Flow Requirement
Does the water system provide fire protection?
| Maximum fire suppression demand for water system or pressure zone (gpm) | [6 empty] | 1500
| Maximum fire suppression duration for water system or pressure zone (hours) | [6 empty] | 2
| Required Fire Suppression Storage (gallons) |  |  |  | - - - - - - - - | - - - - - - - - - | - - - > > > | 180000
(Enter notes here. Verify minimum fire flow and duration with local fire authority.)
Total Water System Requirements (= indoor use + outdoor use + fire flow demand)
MINIMUM REQUIREMENTS FOR WATER SYSTEM
| Source |  | Storage |  | Water Rights
| Per ERC | Total | Per ERC | Total | Per ERC | Total
| (gpd/ERC) | (gpm) | (gallons/ERC) | (gallons) | (ac-ft/yr) | (ac-ft/yr)
| 1044.08 | 554.67 | 526.4 | 583984 | 0.533 | 391.73
Does this system have adequate source capacity per R309-510-7?
IPS points may be assessed for lacking adequate source capacity to meet peak day and/or average yearly flow requirements.
|  | Existing Sources: | 560 | gpm
|  | Required Source Capacity: | 554.67 | gpm
|  | % of Req'd Capacity: | 101%
|  | Difference: | 5.33 | gpm
Does this system have adequate storage capacity per R309-510-8?
IPS points may be assessed for lacking adequate storage capacity.
|  | Existing Storage: | 520000 | gal
|  | Required Storage Capacity: | 583984 | gal
|  | % of Req'd Capacity: | 89.04%
|  | Difference: | -63984 | gal
Non-Community Water Systems, ERCs for Indoor Water Use (*See R309-510, Tables 510-1, 2, and 4, for other facility type calc.)
MINIMUM REQUIREMENTS FOR INDOOR USE
|  |  |  | Source |  | Storage
Facility Type |  |  |  | GPD/person* | Calculated GPD/site or pad | GPD/person | Gallon/site or pad | ERC/site or pad | # of Sites or pads | ERCs
Modern Recreation Camp |  |  |  | 60 | 0 | 30 | 0 | 0 | 0 | 0
Semi-Developed Camp w/ flush toilets |  |  |  | 20 | 0 | 10 | 0 | 0 | 0 | 0
Semi-Developed Camp w/o flush toilets |  |  |  | 5 | 0 | 2.5 | 0 | 0 | 0 | 0
RV Park |  |  |  | N/A | 100 | N/A | 50 | 0.125 | 0 | 0
|  |  | *Number of people per camp site | 0
|  |  |  | Source (GPD/vehicle) | Storage (Gal./vehicle) | ERC/1000 vehicles served | # of Vehicles served | ERCs
Roadway Rest Stop w/ flushometer valves |  |  |  | 7 | 3.5 | 8.75 | 0 | 0
Fable Haven Town
Equivalent Residential Connection Calc. | [5 empty] | Source |  |  | (in gallons per minute)
Existing Residential Connections |  |  | 600 |  |  | WS001 | A Spring |  | 50
[6 empty] | WS005 | B Well |  | 110
Number of Obligated Future ERCs |  |  | 0 |  |  | WS007 | next town wholesale |  | 400
[6 empty] | Total Source Capacity |  |  | 560
[6 empty] | Max. ERC allowed (for indoor use only) |  |  | 1008
[6 empty] | Storage |  |  | (in gallons)
[6 empty] | ST001 | South Tank |  | 100000
[6 empty] | ST002 | East Tank |  | 300000
[6 empty] | ST003 | West Tank |  | 20000
[6 empty] | ST004 | North Tank |  | 50000
[6 empty] | ST005 | Middle Tank |  | 50000
Total Projected Number of ERCs |  |  | 600
(Enter notes here if needed.)
[6 empty] | Total Storage Capacity |  |  | 520000
Enter number of non-residential connections (e.g., 2 factory connections).
Convert "Number of other connections" (Cell E9) to ERCs here. (ERCs of other connection = peak day demand of other connections / 800 gal per day)
Enter estimated irrigated acre per residential lot here.
Enter total irrigated acres of other connections here.
Enter fire flow in gpm.
Enter duration in hours.
Linked to Cell I99 below.
Select Irrigated Zone # from the list (see "Irrigation Demands & Map" tab on the bottom of the screen).
Linked to Cell I118 below.
If applicable, enter number of people per camp site here.
Negative number means (1) additional source capacity is needed , and (2) IPS points should be assessed.
Negative number means (1) additional storage volume is needed, and (2) IPS points should be assessed.
If you need to calculate projected future demand (including existing & future connections), insert this number to Cell I8 "Number of residential connection."
Linked to Cell I8 above.
Diaphragm or air pressure tanks shall not be considered effective storage volume for community systems or NTNC with significant demand.
Linked to Cell C51 above.
Linked to Cell E51 above.

## Additional Notes
Additional Notes
(Use this additional sheet to document calculations related to the DDW Calculation sheet, such as ERCs.)
System Name: | Fable Haven Town | System Number: | 11111
(Enter additional notes here.)

## Irrigation Demands & Map
Irrigation Demands & ERCs
(used in calculations on DDW Calculation sheet)
System Name: |  | Fable Haven Town |  |  | System Number: | 11111
Zone | Peak Day | Avg Year | Storage
| Demand | Demand | Reqmt
3 | 3.39 | 1.66 | 2528
IRRIGATION DEMANDS
(to be added to indoor and fire flow demands)
|  | Avg. Yr. | Storage | Peak
| Peak Day | (ac-ft/yr | Requirement | Instantaneous
zone | (gpm/irr. ac) | per irr. ac.) | (gal/irr. ac) | (gpm/irr. ac)
1 | 2.26 | 1.17 | 1782 | 4.52
2 | 2.8 | 1.23 | 1873 | 5.6
3 | 3.39 | 1.66 | 2528 | 6.78
4 | 3.96 | 1.87 | 2848 | 7.92
5 | 4.52 | 2.68 | 4081 | 9.04
6 | 4.9 | 3.26 | 4964 | 9.8