Proposed Amendment to R309-535-5, Fluoridation

*Note: The proposed amendment to the fluoridation rule below shows new requirements that are not in the current rule but will be included in the proposed amendment underlined and in red. In actuality, the entire proposed amendment will be adopted and will replace the current rule.*

***R309-535-5. Fluoridation.***

This rule does not require the addition of fluoride to drinking water by a public water system. However, a public water system that adds fluoride to drinking water shall comply with the fluoridation facility design and construction requirements of this rule. [NEW]

***Guidance:***

***A public water system may not exceed the primary maximum contaminant level for fluoride of 4.0 mg/L per R309-200-5(1)(c). A public water system that exceeds the secondary maximum contaminant level of 2.0 mg/L must issue the public notification required by R309-220-11.***

***A public water system that chooses to add fluoride to drinking water should comply with the testing, monitoring and reporting requirements established by the local health department.***

***In Salt Lake and Davis counties, the local health departments have established the optimal level of fluoride in drinking water and the fluoridation monitoring and reporting requirements. Currently, the U.S. Department of Health and Human Services recommends an optimal fluoride concentration of 0.7 mg/L in drinking water to reduce cavities and tooth decay.***

1. **General Requirements for all Fluoridation Installations.**

The following requirements apply to all types of fluoridation.

1. Chemicals and Materials.
2. All chemicals used for fluoridation shall be certified to comply with ANSI/NSF Standard 60.
3. Materials used for fluoridation equipment shall be compatible with chemicals used in the fluoridation process.
4. Metal parts used in fluoridation equipment and present in the fluoridation room shall be corrosion resistant.[NEW]
5. Lead weights shall not be used in fluoride chemical solutions to keep pump suction lines at the bottom of a day or bulk storage tank.

***Guidance: Acid-resistant floor coating or a containment structure should be provided for areas likely to have acid spills.***

1. Chemical Storage.
2. Fluoride chemicals shall be stored in covered or sealed containers, inside a building, and away from heat.[NEW]
3. Fluoride chemicals shall not be stored with incompatible chemicals.
4. Bags or other containers for dry materials shall be stored on pallets.
5. Fiber drums for storing dry materials shall be kept closed to keep out moisture.
6. A solution tank shall be labeled to identify the contents of the tank.[NEW]
7. Secondary Containment.[NEW]
8. Secondary containment shall be provided for tanks containing corrosive fluoride solutions.[NEW]
9. Secondary containment shall be sized to contain the quantity of solution handled.[NEW]
10. Secondary containment shall be designed to be acid resistant.[NEW]

***Guidance: Secondary containment may consist of curbs, sumps, double-walled tanks, etc.***

1. Means to Measure.
2. A means to measure the flow of treated water shall be provided.
3. A means shall be provided to measure the solution level in a tank and the quantity of the chemical used.

***Guidance: The means to measure the solution level in a tank may include a liquid level indicator, a calibrated level gauge on the side of a translucent tank, weight scales, etc.***

1. A sampling point shall be provided downstream of the fluoridation facility for measuring the fluoride level of treated water.[NEW]
2. Fluoride Feed Pump
	1. Sizing of fluoride feed pumps shall consider prevention of fluoride overfeed and operation efficiency.[NEW]
	2. A fluoride feed pump shall have an anti-siphon device.
3. Electrical Outlet for Fluoride Feed Pump
4. The electrical outlet used for a fluoride feed pump shall have interlock protection by being wired electrically in series with the well or service pump, such that the feed pump is only activated when the well or service pump is on.
5. The fluoride feed pump shall not be plugged into a continuously active ("hot") electrical outlet.[NEW]
6. Fluoride Injection
	1. The fluoride injection line shall enter at a point in the lower one-third of the water pipe[NEW], and the end of the injection line shall be in the lower half of the water pipe.
	2. The fluoride injection point shall allow adequate mixing.[NEW]
	3. The fluoride injection point shall not be located upstream of lime softening, ion exchange, or other processes that affect the fluoride level.
	4. Each injector shall be selected based on the quantity of fluoride to be added, water flow, back pressure, and injector operating pressure.[NEW]

***Guidance: The design should minimize localized corrosion near the injection point.***

* 1. If injecting fluoride under pressure, a corporation stop and a safety chain shall be used at the fluoride injection point to secure the injection line.[NEW]
	2. An anti-siphon device shall be provided for all fluoride feed lines at the injection point.
1. Minimize Fluoride Overfeed
	1. In addition to the feed pump control, a secondary control mechanism shall be provided to minimize the possibility of fluoride overfeed. It may be a day tank, liquid level sensor, SCADA control, a flow switch, etc.

***Guidance: The intent of the day tank is to limit the fluoride supply to the feed pump, especially if a large-size bulk tank is present. It is recommended that the day tank be sized to hold no more than 3 days of supply.***

* 1. For fluoridation facilities that do not have operators on site, a day tank is required to minimize fluoride overfeed, unless two alternative secondary controls are provided.[NEW]

***Guidance: For example, a fluoridation facility without operators on site may use both the bulk tank liquid level sensor and the treated water fluoride level SCADA data as secondary controls.***

***Guidance: To avoid fluoride overfeed, a flooded suction line should be avoided for the fluoride feed pump. The elevation of a fluoride feed pump should be based on pump priming requirements and suction head limitations.***

1. Housing

Fluoridation equipment shall be housed in a secure building that is adequately sized for handling and storing fluoride chemicals.[NEW]

1. Heating, Lighting, Ventilation[NEW]
	1. The fluoridation building shall be heated, lighted and ventilated to assure proper operation of the equipment and safety of operator.[NEW]
	2. The ventilation in the fluoride operating area shall provide at least six complete room-air changes per hour.[NEW]
	3. The fluoride operating area shall be vented to outside atmosphere and away from air intakes.[NEW]
	4. Separate switches for fans and lights in the fluoride operating area shall be provided. The switches shall be located outside of, or near, the entrance to the fluoride operating area, and shall be protected from vandalism.[NEW]
2. Cross Connection Control

Cross connection shall be eliminated by physical separation, an air gap, or an approved and properly operating backflow prevention assembly.[NEW]

1. **Additional Requirements for Fluorosilicic Acid Installations.**
2. Fluorosilicic acid shall not be diluted manually on site before injection.[NEW]
3. Solution Tank Vents.[NEW]
4. A solution tank shall be adequately vented to the outside atmosphere away from air intakes, above grade, and where least susceptible to contamination.[NEW]
5. A bulk tank shall not share a vent with a day tank if there is a risk of solution overflow from the bulk tank to the day tank.[NEW]
6. A non-corrodible fine mesh (No. 14 or finer) screen shall be placed over the discharge end of a vent.[NEW]
7. If separate rooms are provided in a fluoride building constructed after January 1, 2017, the design shall include a view window between the control room and the fluorosilicic acid operating area.[NEW]

***Guidance: It is recommended to have a separate room for the fluoride operating area due to possible damage from fluoride chemicals and vapors to other equipment.***

1. Emergency eyewash stations and showers shall be provided.
2. A neutralizing chemical shall be available on site to handle small quantity accidental acid spills.[NEW]

***Guidance: The immediate use of a neutralizing chemical to handle an accidental acid spill is only suitable for small quantity spills during operation or maintenance, for example, minor spillage from the quick connect during unloading. For large quantity acid spills, the secondary containment is the primary means of containing the acid to allow proper handling of the acid later on.***

1. The use of personal protective equipment (PPE) is required when handling fluorosilicic acid, and shall include the following:
	1. Full-face shield and splash-proof safety goggles
	2. Long gauntlet acid-resistant rubber or neoprene gloves with cuffs
	3. Acid-resistant rubber or neoprene aprons
	4. Rubber boots
2. **Additional Requirements for Fluoride Saturator Installations.**
3. A water meter shall be provided on the make-up water line for a saturator so that calculations can be made to confirm that the proper amounts of fluoride solution are being fed. This meter and the master meter shall be read daily and the results recorded.[NEW]
4. The minimum depth of undissolved fluoride chemical required to maintain a saturated solution shall be marked on the outside of the saturator tank.[NEW]

***Guidance: Sodium fluorosilicate should not be used in saturators due to its poor solubility.***

1. The saturator shall not be operated in a manner that undissolved chemical is drawn into the pump suction line.[NEW]
2. The make-up water supply line shall, at a minimum, terminate at least two pipe diameters above the solution tank or have backflow protection.
3. Make-up Water Softening
	1. The make-up water used for sodium fluoride saturators shall be softened whenever the hardness exceeds 75 mg/L.
	2. A sediment filter (20 mesh) shall be installed in the make-up water line going to the saturator. The filter shall be placed between the softener and the water meter.[NEW]
4. Dust Control.

Provisions shall be made to minimize the creation of fluoride dust during the transfer of dry fluoride compounds.

1. Air exhausted from fluoride handling equipment shall discharge through a dust filter to the atmosphere outside of the building.
2. Provisions shall be made to minimize dust when disposing of empty bags, drums or barrels.

1. A floor drain shall be provided to facilitate floor cleaning.
2. Emergency eyewash shall be provided.
3. The use of personal protective equipment (PPE) is required when handling dry chemicals and shall include the following:
	1. National Institute for Occupational Safety and Health (NIOSH) approved particulate respirator with a soft rubber face-to-mask seal and replaceable cartridges
	2. Chemical dust-resistant safety goggles
	3. Acid-resistant gloves
	4. Acid-resistant rubber or neoprene aprons
	5. Rubber boots
4. **Additional Requirements for Fluoride Dry Feed Installations.**
5. Volumetric and gravimetric dry feeders shall include a solution tank.[NEW]
6. A mechanical mixer shall be installed in the solution tank.[NEW]
7. Dust Control.

Provisions shall be made to minimize the creation of fluoride dust during the transfer of dry fluoride compounds.

1. If a hopper is provided, it shall be equipped with a dust filter and an exhaust fan that places the hopper under negative pressure.

1. Air exhausted from fluoride handling equipment shall discharge through a dust filter to the atmosphere outside of the building.
2. Provisions shall be made to minimize dust when disposing of empty bags, drums or barrels.
3. A floor drain shall be provided to facilitate floor cleaning.
4. Emergency eyewash shall be provided.
5. The use of personal protective equipment (PPE) is required when handling dry chemicals and shall include the following:
6. National Institute for Occupational Safety and Health (NIOSH) approved particulate respirator with a soft rubber face-to-mask seal and replaceable cartridges
7. Chemical dust-resistant safety goggles
8. Acid-resistant gloves
9. Acid-resistant rubber or neoprene aprons
10. Rubber boots

Current R309-535-5, Fluoridation

*Note: The current fluoridation rule below shows the requirements that will not be included in the proposed amendment struck through and in red. In actuality, the entire current rule will be deleted and replaced by the proposed amendment.*

***R309-535-5. Fluoridation.***

Sodium fluoride, sodium silicofluoride and fluorosilicic acid shall conform to the applicable AWWA standards and/or ANSI/NSF Standard 60. [NOT IN PROPOSED AMENDMENT]

**(1) Fluoride compound storage.**

Fluoride chemicals shall be isolated from other chemicals to prevent contamination. Compounds shall be stored in covered or unopened shipping containers and shall be stored inside a building. [NOT IN PROPOSED AMENDMENT] Bags, fiber drums and steel drums shall be stored on pallets.

**(2) Chemical feed equipment and methods.**

In addition to the requirements in R309-525-11 "Chemical Addition", fluoride feed equipment shall meet the following requirements:

(a), [NOT IN PROPOSED AMENDMENT]

(b), [NOT IN PROPOSED AMENDMENT]

(c) fluoride compound shall not be added before lime-soda softening or ion exchange softening,

(d) the point of application of fluorosilicic acid, if into a horizontal pipe, shall be in the lower half of the pipe,

(e), [NOT IN PROPOSED AMENDMENT]

(f) [NOT IN PROPOSED AMENDMENT]

(g) a device to measure the flow of water to be treated is required,

(h) the dilution water pipe shall terminate at least two pipe diameters above the solution tank,

(i) water used for sodium fluoride dissolution shall be softened if hardness exceeds 75 mg/l as calcium carbonate,

(j), [NOT IN PROPOSED AMENDMENT]

(k) the electrical outlet used for the fluoride feed pump shall have a nonstandard receptacle and shall be interconnected with the well or service pump,

(l). [NOT IN PROPOSED AMENDMENT]

(m) lead weights shall not be used in fluoride chemical solutions to keep pump suction lines at the bottom of a day or bulk storage tank.

**(3) Secondary controls.**

Secondary control systems for fluoride chemical feed devices shall be provided as a means of reducing the possibility for overfeed; these may include flow or pressure switches or other devices.

**(4) Protective equipment.**

Personal protective equipment as outlined in R309-525-11(10) shall be provided for operators handling fluoride compounds. Deluge showers and eye wash devices shall be provided at all fluorosilicic acid installations.

**(5) Dust control.**

(a) Provision must be made for the transfer of dry fluoride compounds from shipping containers to storage bins or hoppers in such a way as to minimize the quantity of fluoride dust which may enter the room in which the equipment is installed. The enclosure shall be provided with an exhaust fan and dust filter which place the hopper under a negative pressure. Air exhausted from fluoride handling equipment shall discharge through a dust filter to the outside atmosphere of the building.

(b) Provision shall be made for disposing of empty bags, drums or barrels in a manner which will minimize exposure to fluoride dusts. A floor drain shall be provided to facilitate the hosing of floors.

 [NOT IN PROPOSED AMENDMENT]