# R309-540. Facility Design and Operation: Pumping Facilities.

## R309-540-1. Purpose.

The purpose of this rule is to provide specific requirements for the design and operation of drinking water pumping facilities. It is intended to be applied in conjunction with rules R309-500 through R309-550. Collectively, these rules govern the design, construction, operation and maintenance of public drinking water system facilities. These rules are intended to assure that such facilities are reliably capable of supplying adequate quantities of water which consistently meet applicable drinking water quality requirements and do not pose a threat to general public health.

## R309-540-2. Authority.

This rule is promulgated by the Drinking Water Board as authorized by Title 19, Environmental Quality Code, Chapter 4, Safe Drinking Water Act, Subsection 104(1)(a)(ii) of the Utah Code and in accordance with 63G-3 of the same, known as the Administrative Rulemaking Act.

## R309-540-3. Definitions.

Definitions for certain terms used in this rule are given in R309-110 but may be further clarified in this rule.

## R309-540-4. General.

The following requirements apply to all pumping facilities including pumps, pump stations, and hydropneumatic systems. Pumping facilities shall be adequately sized and be designed to maintain the quality of the water and to meet minimum pressure requirements.

### (1) Location and Accessibility.

(a) A pumping facility shall be designed and operated to meet the following requirements:

(i) The facility may not be located at a site that negatively affects drinking water quality.

(ii) The site shall be compatible with the hydraulics of the water system.

(iii) The site shall be graded to direct surface runoff away from the facility.

(iv) The facility shall be accessible at all times unless the facility can be taken out of service during periods of inaccessibility.

(v) The facility shall be protected from vandalism and unauthorized entry.

### (2) Appurtenances.

(a) Valves.

Valves for pumping facilities shall be designed and operated to meet the following requirements.

(i) Isolation valves shall be included for operation, maintenance, and repair of the pumping equipment.

(ii) Foot valves in wet wells shall have a net valve area of at least 2 1/2 times the area of the suction pipe and there shall be a positive-acting check valve on the discharge side between the pump and the shut-off valve.

(iii) The open end of a vent on an air relief valve shall be downturned and covered with a #14 mesh non-corrodible screen. The end of a vent shall terminate in the following location:

(A) Six inches above the floor, if the valve is located in a building

(B) 12 inches above the top of the water line, if the valve is located in a below grade chamber that is not subject to flooding

(C) 12 inches above grade, if the valve is located in a below grade chamber that is subject to flooding

(b) Piping.

Piping for pumping facilities shall be designed to meet the following requirements:

(i) Friction losses shall be minimized.

(ii) Piping shall not be subject to contamination.

(iii) Watertight joints shall be provided.

(iv) Protection against surge or water hammer shall be provided along with suitable restraints if necessary.

- Controls.

Controls for pumping facilities shall be designed and operated to meet the following requirements:

(i) The pump and accessories shall operate at the rated capacity.

(ii) Where two or more pumps are installed, provisions shall be made for alternation of the pumps.

(iii) Provisions shall be made to prevent energizing the pump motor in the event of a backspin cycle.

(iv) Electrical controls shall be protected against flooding.

(v) Provisions shall be made to prevent surge pressures from activating controls that switch on pumps or activate other equipment outside the normal design cycle of operation.

(vi) Pump control equipment shall have proper overload protection for the air temperature encountered.

- Standby Power.

A community water system that relies solely on a pump to supply water to the distribution system shall provide a redundant power supply. A redundant power supply may include a transfer switch for auxiliary power such as a generator or a power supply service with coverage from two independent substations.

- Water Pre-Lubrication.

If automatic pre-lubrication of pump bearings is needed and an auxiliary direct drive power supply is provided, the pre-lubrication line shall be provided with a valved bypass around the automatic control so that the bearings can, if necessary, be lubricated manually before the pump is started or the pre-lubrication controls shall be wired to the auxiliary power supply.

## R309-540-5. Pumps.

- Capacity.

Pumping facility shall be sized to meet the peak day demand of the specific portion of the distribution system served, or it shall meet the operating conditions if not serving the distribution system.

Guidance: a second pump is recommended if the pump delivers a sole source of water.

(b) Pump Motor.

Pump motors shall meet the following requirements:

(i) The pump motor shall be sized to meet the operating conditions without dangerous overloading.

(ii) The pump shall be driven by prime movers able to meet the maximum horsepower condition of the pumps without use of service factors.

(c) Suction Lift.

Suction lift, where possible, should be avoided. If suction lift is necessary, it shall be within the pump manufacturer's recommended limits and provisions shall be made for priming the pumps.

(d) Priming.

Where pumps require priming, the following requirements shall be met:

(i) Priming water shall not be of lesser sanitary quality than that of the water being pumped.

(ii) A means shall be provided to prevent back siphonage.

(iii) When an air-operated ejector is used for vacuum priming, the screened intake shall draw clean air from a point at least 10 feet above the ground or other source of possible contamination.

(e) Water Seal.

Where pumps use water seals, the seals shall meet the following requirements:

(i) They may not be supplied with water of a lesser sanitary quality than that of the water being pumped.

(ii) When pumps are sealed with potable water and are pumping water of lesser sanitary quality, the water for the seal shall be provided with a break tank open to atmospheric pressure, and have an air gap of at least six inches or two pipe diameters, whichever is greater, between the feeder line and the spill line of the tank.

## R309-540-6. Booster Pumps Serving the Distribution System.

(a) Booster pumps shall be designed and operated to meet the following requirements:

(i) Negative pressure may not be produced in suction lines.

(ii) The automatic cutoff pressure shall be at least 10 psi in the suction line.

(iii) Automatic or remote control devices shall have a range between the start and cutoff pressure that will prevent excessive cycling.

(iv) A bypass shall be available.

- Inline booster pumps (pumps withdrawing water directly from distribution lines without the benefit of storage and feeding such water directly into other distribution lines rather than storage) shall be designed and operated to meet the following requirements:

(i) At least two pumping units shall be provided.

(ii) The pumps shall be accessible for servicing and repair.

(iii) The intake pressure shall be at least 20 psi when the pump or pumps are in normal operation.

(c) A public water system may not rely on individual service connection booster pumps to meet minimum pressure requirements.

Guidance: Refer to Guidance found in R309-550-11(3)

## R309-540-7. Pump Stations.

(a) If a building structure is provided for pumping facilities it shall be designed to meet the following requirements:

(i) Adequate space shall be provided for the safe servicing of all equipment and, if needed, the installation of additional pumps.

(ii) The building shall be durable.

(iii) Access to the pump station shall be six inches above the surrounding ground and the station located at an elevation which is a minimum of three feet above the 100-year flood elevation, or three feet above the highest recorded flood elevation, whichever is higher, or protected to such elevations.

(iv) Underground facilities shall be waterproof.

(v) Interior floors shall be drained in such a manner that the quality of drinking water contained in a wet well will not be endangered.

(vi) A means shall be provided for handling drainage from pump glands.

(b) Wet wells shall be designed to meet the following requirements:

(i) Construction shall be watertight.

(ii) Floors shall be sloped to permit removal of water and sediment.

(iii) Openings shall be covered and protected against contamination.

    - Provisions shall be made for servicing or removal of heavy or bulky equipment.

Guidance: for large facilities, provisions for servicing or removal of heavy or bulky equipment may include crane-ways, hoist beams, eye-bolts, openings in floors or roofs, etc.

    - Stairways and ladders shall be designed to meet the following requirements:

(i) Safe access shall be provided between all floors and in pits or compartments that must be entered.

(ii) Added features shall provide for the safety of the operator, for example, by providing handrails on stairways and non-slip treads on steps.

Guidance: Ramps are preferred in areas where there is frequent traffic or where supplies are transported by hand. Where ramps are not possible, stairs are preferred to ladders.

(e) Adequate heating and lighting shall be provided for the safety and comfort of the operator and the safe and efficient operation of the equipment.

Guidance: In pump houses not occupied by personnel, only enough heat need be provided to prevent freezing of equipment or treatment process.

(f) Ventilation shall meet the following requirements:

(i) Forced ventilation of at least six changes of air per hour shall be provided for rooms, compartments, pits and other enclosures below ground floor and for any area where unsafe conditions may develop.

(ii) Existing local and state codes shall be followed.

Guidance: In areas where excess moisture could cause hazards to safety or damage to equipment, means for dehumidification should be provided.

(g) Automatic and remote-controlled stations shall meet the following requirements:

(i) Remote-controlled stations shall have signaling apparatus of proven performance.

(ii) Installation of electrical equipment shall conform with the applicable state and local electrical codes and the National Electrical Code.

### Guidance: An automatic station should be provided with an automatic signaling apparatus which will report when the station is out of service.

(h) Gauges.

Each pump station shall be designed to include the following gauges:

(i) The discharge line shall have a standard pressure gauge or an alternative means of measuring pressure on the discharge line.

(ii) The suction line shall have a compound gauge (capable of indicating negative pressure or vacuum as well as positive pressure) or an alternative means of measuring pressure.

Guidance: It is recommended that larger pumping stations have indicating, totalizing, and recording metering of the total water pumped and recording pressure gauges.

## R309-540-8. Hydropneumatic Systems.

### (1) General.

(a) Pressure tanks shall comply with ANSI/NSF Standard 61.

(b) Community water systems shall not use hydropneumatic tanks to meet the water storage sizing requirements in R309-510-8.

### Guidance: This section applies to three common types of hydropneumatic tanks: air-over-water pressure tanks, diaphragm pressure tanks, and bladder pressure tanks.

### Guidance: Pressure tanks dedicated for fire suppression service are not considered to be hydropneumatic tanks serving drinking water systems

### (2) Location.

(a) A hydropneumatic pressure tank shall be located above ground if possible.

(b) If pressure tanks and appurtenances are located below ground, adequate provisions for drainage, ventilation, access, maintenance, and flood protection shall be provided, and the electrical controls shall be located above grade so as to be protected from flooding.

### (3) Operating Pressures.

A means of monitoring the operating pressures of a hydropneumatic tank shall be provided.

### (4) Bypass Piping.

The hydropneumatic system design shall include bypass piping and isolation valves to allow one or more of the pressure tanks to be serviced without affecting the availability of the remaining units.

### (5) Redundancy.

(a) When used to maintain minimum pressures within the distribution system, a community water system shall have a means of providing redundancy to allow the tanks to be taken off line or serviced.

(b) At least two units shall be provided for community water systems if the hydropneumatic system is the only means to maintain minimum pressures in the distribution system.

### (6) Sizing.

The minimum volume of a hydropneumatic tank shall be sized to avoid excessive pump cycling.

Guidance:  The number of allowable starts varies with the design speed of the motor and the motor size. Follow the manufacturer’s recommendations to avoid excessive pump cycling.

Guidance: As a rule-of-thumb the minimum volume of the hydropneumatic tank should be at least five times the capacity of the pump(s), rated in gpm. For example, a 200 gpm pump or combination of pumps should have a 1,000 gallon pressure tank.

### (7) Air-Over-Water Pressure Tanks.

(a) General.

Large air-over-water pressure tanks shall have an access manhole, a drain, a pressure gauge, a water sight glass, an automatic or manual air blow-off, a means for adding air, and pressure operated start-stop controls for the pumps.

(b) Air Supply for Pressure Tanks.

(i) Air delivered by a compressor to the pressure tank shall be adequately filtered, oil free, and be of adequate flow rate.

(ii) An air intake shall be screened and draw clean air from a point above the ground and free of possible contamination.

(iii) Discharge piping from air relief valves shall be screened and designed to eliminate the possibility of contamination.

(c) Water Seal.

(i) For air pressure tanks without an internal diaphragm the volume of water remaining in an air pressure tank at the lower pressure setting shall be sufficient to provide an adequate water seal at the outlet to prevent the leakage of air.

Guidance: To prevent the formation of a vortex, a covering baffle may be installed over a vertical bottom outlet large enough to limit the peripheral velocity of approach to the baffle to 0.5 ft/sec or less. At low absolute pressure the depth of water over the top of the baffle should be about one outlet pipe velocity head or greater.

(d) Water Seal Depth.

The minimum water seal depths shall be as follows.

(i) Horizontal outlets shall maintain sufficient depth, as measured from the centerline of the horizontal outlet pipe, such that the depth is greater than or equal to the sum of [d] and [twice the value v squared divided by 2g]. [Depth ≥ d + (2v2/2g)]

(ii) For vertical outlets, if unbaffled, the depth shall be the same as in (i) except measured from the pipe outlet; if baffled, the depth shall be greater than or equal to the value v squared divided by 2g. [Depth ≥ (v2/2g)]

where the following values are used in the equations above:

v = the axial velocity in the pipe outlet for the peak instantaneous demand flow rate of the system.

d = the diameter of the outlet pipe in feet

g = the gravitational constant of 32.2 feet/sec/sec.

Guidance: For either horizontal or vertical outlets, the pipe outlet itself should be large enough to limit the maximum axial velocity in the pipe to 4.0 ft/sec or less. The use of anti-swirl vanes is always desirable.

KEY: drinking water, pumps, hydropneumatic systems, individual home booster pumps

Date of Enactment or Last Substantive Amendment:

Notice of Continuation: March 13, 2015

Authorizing, Implemented, or Interpreted Law: 19-4-104