## Dist Sys Checklist - Draft
| Distribution System |  |  |  |  | Utah DEQ | Yes
| Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
| Project Information (to be completed by the applicant) |  | Professional Engineer Responsible for Design (to be completed by the design PE)
| PWS Name: |  | Name:
| PWS ID: |  | Registration No.:
| Project Description: |  | Phone No.:
Email:
Engineer's Certification:
By checking the following box, I certify that the information that I have provided
on this form is true and accurate to the best of my knowledge.
| DDW Plan Review Information (to be completed by DDW review engineer) |  | DDW Plan Review Workflow (to be completed by DDW review engineer)
| Project File Number: |  | Review completed and checklist below updated:
| Plan Review Engineer: |  | Written correspondence based on review sent to PWS:
Instructions: in the appropriate column below, orange for the Design Engineer and blue for DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain a response.
|  | Summary of Requirement |  | Design | Review
UAC Rule |  |  |  | Engineer | Engineer | Notes
General Requirements
R309-500-6 (2)(b) |  | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) |  | Plans and specifications stamped, dated and signed by PE
R309-500-6 (2)(e) |  | Alternate designs included that require the Director to grant exceptions to rules
N/A |  | Project will resolve existing physical deficiencies
Hydraulic Modeling
R309-511-4 (1)(b) |  | Hydraulic modeling results certified by PE
R309-511-4 (2)(d) |  | Hydraulic Model Design Elements Report provided
R309-511-4 (2)(f) |  | System Capacity and Expansion Report provided
R309-550-5 (3)(b) |  | Hydraulic analysis provided for entire distribution system (>50% distribution upgrade/new distribution system)
R309-550-5 (3)(c) |  | Hydraulic modeling report per R309-511 provided
Distribution System Pressure
R309-105-9(2)(a) |  | Minimum 20 psi peak day demand during fire flow
R309-105-9(2)(b) |  | Minimum 30 psi peak instantaneous demand
R309-105-9(2)(c) |  | Minimum 40 psi peak day demand
R309-550-5 (1)(a) |  | Minimum pressures maintained at points of connection under all flow conditions
R309-550-5 (1)(b) |  | Pressure reducing devices on new mains where static pressure exceeds 150 psi
Fire Flow
R309-510-9 (1) |  | Distribution system sized for fire flow rate and duration according to local fire authority letter
R309-550-5 (5)(a) |  | Distribution system designed to meet fire flow requirements per local fire code official
R309-550-5 (5)(b) |  | Fire hydrant location per state-adopted fire code
R309-550-5 (5)(c) |  | Designed to meet minimum pressures throughout distribution system during fire flow
R309-550-5 (5)(d) |  | Minimum 6-inch diameter fire hydrant laterals
R309-550-6 (5)(a) |  | Fire hydrant drains separate from sewers
R309-550-6 (5)(a) |  | Fire hydrant drains greater than 10 feet from sanitary sewers
R309-550-6 (5)(a) |  | Fire hydrant drains greater than 10 feet from storm sewers
R309-550-6 (5)(b) |  | Fire hydrant laterals include auxiliary valves
R309-550-6 (5)(c) |  | Adequate fire hydrant drainage - acceptable natural soil, gravel pack, or dry well
Pipe Sizing
R309-510-9 (2) & (3) |  | Distribution system sized for peak instantaneous demand
R309-550-5 (2) |  | Designed using minimum flow rates for fire flow and peak instantaneous demand per R309-510
R309-550-5 (3)(a) |  | Water main size based on hydraulic analysis of flow demands and pressure requirements
R309-550-5 (4) |  | Minimum water main size: 4" w/o fire hydrants; 8" w/ fire hydrants; 6" w/ fire hydrants & hydraulic analysis
Cross Connection Control
R309-105-12(1) |  | Backflow prevention on cross connections
R309-550-6 (8)(b) |  | Backflow device installation conforms to state plumbing code
R309-550-9 (1) |  | Physical cross-connections absent
R309-550-9 (2) |  | Condensate or cooling water from engine jackets or heat exchangers separate from drinking water supply
R309-550-9 (3) |  | Interconnection with another drinking water system approved by Director
Soil and Ground Water
R309-550- 5 (6) |  | Soil characteristics considered for water main burial
R309-550-5 (9) |  | Distribution system materials appropriate for corrosive soil or water
R309-550-5 (10)(a)&(b) |  | Non-permeable distribution system materials specified in areas of contamination
R309-550-5 (11) |  | DDW-specified design requirements used for water mains near contamination areas
Design and Construction
R309-550-5 (6) |  | Special design and burial for CWS water mains in geologic hazard areas
R309-550-5 (7)(a) |  | Dead ends minimized by making appropriate tie-ins
R309-550-5 (7)(b) |  | Unavoidable dead ends equipped with fire hydrants, flush hydrants, or blow-off valves
R309-550-5 (7)(b) |  | Dead end flushing devices sized for minimum velocity of 2.5 fps in the water main
R309-550-5 (7)(b) |  | Flushing devices separate from sewers
R309-550-5 (8) |  | Maximum interval of 500' between isolation valves in commercial districts
R309-550-5 (8) |  | Maximum interval of one block or 800' between isolation valves in non-commercial districts
R309-550-5 (8) |  | Maximum interval of 1 mile between isolation valves in areas of widely scattered customers & no future development
R309-550-6 (1) |  | NSF/ANSI 61 certification specified for drinking water system components
R309-550-6 (2)(a) |  | Asbestos-cement pipe absent
R309-550-6 (2)(b) |  | Lead-free pipes and fittings specified
R309-550-6 (3) |  | NSF/ANSI 61, AWWA C104-A21.4-08 through C550-05, and C900-07 through C950-07 conformance specified
R309-550-8 (1)(a) |  | Specs incorporate manufacturer's installation procedures or AWWA C600-10 for ductile iron pipe
R309-550-8 (1)(b) |  | Specs incorporate manufacturer's installation procedures or ASTM D2774 and AWWA M23 for PVC pipe
R309-550-8 (1)(c) |  | Specs incorporate manufacturer's installation procedures or ASTM D2774 and AWWA M55 for HDPE pipe
R309-550-8 (1)(d) |  | Specs incorporate manufacturer's installation procedures or AWWA C604-11 for steel pipe
R309-550-8 (2) |  | Continuous uniform bedding specified for buried piping
R309-550-8 (3)(a) |  | Maximum 3/4-inch particle size specified for backfill material for plastic pipe
R309-550-8 (3)(b) |  | Specs limit stones to maximum 2-inch diameter in backfill material for ductile iron pipe
R309-550-8 (4) |  | Specs prohibit dropping pipe into trench
R309-550-8 (5) |  | Minimum cover specified to prevent freezing
R309-550-8 (6) |  | Thrust blocking, anchoring, tie rods, or restraints specified for tees, bends, plugs, and hydrants
R309-550-8 (6) |  | Pipe restraints properly sized for expected forces
R309-550-8 (7) |  | Pressure and leak testing specified per AWWA C600-10
R309-550-8 (9) |  | Specs require open ends of pipe to be sealed at end of day's construction
R309-550-8 (10) |  | Procedures specified for flushing, disinfection, and microbiological testing (flushing per AWWA C651-05)
Valves and Valve Chambers
R309-550-6 (6)(a) |  | Air relief valves/hydrants at distribution system high points
R309-550-6 (6)(b) |  | Automatic valve air relief vent pipe designed with non-corrodible #14 mesh screen cover
R309-550-6 (6)(b) |  | Downturned automatic valve air relief vent at least 1 foot above grade
R309-550-6 (6)(b) |  | Automatic valve air relief vent at least 1 foot above pipe in chamber with no flooding & adequate drainage
R309-550-6 (6)(c) |  | Air Relief/Blow Off Valves separate from sewers
R309-550-6 (6)(d) |  | Adequate number of hydrants or blow-off valves for water-line flushing
R309-550-6 (6)(e) |  | Air relief valve protected from freezing
R309-550-6 (6)(e) |  | Shut-off valve provided to service air relief valve
R309-550-6 (7)(a) |  | Valve or meter chambers separate from storm drains
R309-550-6 (7)(a) |  | Valve or meter chambers separate from sanitary sewers
R309-550-6 (7)(b) |  | Valve or meter chambers drain to daylight , have absorption pit, or use sump pumps
R309-550-6 (8)(a)(i) |  | Isolation valves on both sides of each pressure reducing valve
R309-550-6 (8)(a)(ii) |  | Parallel PRV lines provided to accommodate low and high flows
Water/Sewer Separation
R309-550-7 (1)(a) |  | Minimum 10 foot lateral separation between water and sanitary sewer lines
R309-550-7 (1)(a) |  | Water line a minimum of 18 inches above sanitary sewer line where they cross
R309-550-7 (1)(b) |  | Water and sewer lines installed in separate trenches
R309-550-7 (1)(c) |  | Information provided to support minimum 6' water/sewer lateral separation distance due to local conditions
R309-550-7 (1)(d) |  | Exception request to minimum separation standards provided per R309-105-6 (2)(b)
R309-550-7 (3)(a) |  | Greater water/sewer separation distance specified in areas of high groundwater
R309-550-7 (3)(b) |  | Minimum 20 foot water/sewer separation required where water lines may become unpressurized
R309-550-7 (3)(c) |  | Measures specified to prevent/minimize disturbance of existing water or sewer lines
R309-550-7 (3)(d) |  | Pipe material reflects corrosive conditions and inability to meet minimum separation between water/sewer
R309-550-7 (3)(e)(i) |  | New sewer force main enclosed in continuous sleeve within 10 feet of water main crossing
R309-550-7 (3)(e)(ii) |  | Minimum rated working pressure of 200 psi specified for new water main crossing over existing sewer
R309-550-7 (4) |  | Water service laterals crossing sewer mains/laterals meet minimum separation distances
R309-550-12 (1) |  | Unpressurized flows in transmission lines minimized
R309-550-12 (2) |  | Unpressurized transmission lines located greater than 20 feet from concentrated source of pollution
R309-550-12 (2) |  | Unpressurized transmission lines located outside of boggy areas and areas of water ponding
Surface Water Crossings
R309-550-8 (8)(a) |  | Lines above open water adequately supported and anchored
R309-550-8 (8)(a) |  | Lines above open water protected from damage and freezing
R309-550-8 (8)(a) |  | Lines above open water accessible for repair and replacement
R309-550-8 (8)(b)(i) |  | Minimum 2 feet of cover specified for lines for underwater crossing
R309-550-8 (8)(b)(ii)(A) |  | Restrained joints below water and flexible joints at water edges specified for crossings greater than 15 feet
R309-550-8 (8)(b)(ii)(B) |  | Isolation valves specified on both sides of line crossing under water (beyond high ground water and flood zone)
R309-550-8 (8)(b)(ii)(C) |  | Sample taps specified upstream and downstream on line crossing under water
R309-550-8 (8)(b)(ii)(D) |  | Pressure testing specified for line crossing under water
Service Connections
R309-550-6 (8)(c) |  | Meter installation conforms to state plumbing code and local standards
R309-550-11 (2)(a) |  | Water services and plumbing conform to state-adopted plumbing code
R309-550-11 (2)(b) |  | Lead-free pipes and fittings specified for plumbing
R309-550-11 (2)(b) |  | Specs require plumbing pipes and fittings to be certified to meet NSF/ANSI 372 or NSF/ANSI 61, Annex G
R309-550-11 (3) |  | Individual service-connection booster pumps absent
R309-550-11 (4)(a) |  | Specs require service lines to be capped until connected
R309-550-11 (5) |  | Connection between service meter and home conforms to state-adopted plumbing code
Wastewater Disposal
R309-500-10 |  | Method of wastewater disposal approved by DWQ or LHD (new systems/subdivision additions)
Engineer's Certification
Yes
Yes