## Dist Sys Checklist
Distribution System |  |  |  |  | Utah DEQ | Yes
Construction Plan Review Checklist |  |  |  |  | Division of Drinking Water | No
N/A
Project Information (to be completed by the applicant) |  | Professional Engineer Responsible for Design (to be completed by the design PE)
PWS Name: |  | Name:
PWS ID: |  | Registration No.:
Project Description: |  | Phone No.:
Email:
Engineer's Certification:
By checking the following box, I certify that the information that I have provided
on this form is true and accurate to the best of my knowledge.
DDW Plan Review Information (to be completed by DDW review engineer) |  | DDW Plan Review Workflow (to be completed by DDW review engineer)
Project File Number: |  | Review completed and checklist below updated:
Plan Review Engineer: |  | Written correspondence based on review sent to PWS:
Instructions: In the appropriate column below, orange for the Design Engineer and blue for DDW Review Engineer, select a response from the dropdown menu indicating whether each requirement listed is addressed in the plans and specs. Add Notes if needed to explain responses. Consult the UAC rules cited to fully understand the details of the regulatory requirements; the summaries below are not meant to replace the rules.
UAC Rule | Summary of Rule Requirement |  | Design Engineer | Review Engineer | Notes
Engineer
General Requirements
R309-500-6 (2)(b) | Plans and specifications sufficiently detailed to assure properly constructed project
R309-500-6 (2)(c) | Plans and specifications stamped, dated, and signed by PE
R309-500-6 (2)(e) | Alternate designs included that require the Director to grant exceptions to rules
R309-500-10 | Method of wastewater disposal approved by DWQ or LHD (new water systems/subdivision additions)
N/A | Project will resolve existing physical deficiencies
Hydraulic Analysis
R309-511-4 (1)(a)(i)(A-G) | Certification and hydraulic model report unnecessary (if project type is listed in R309-511-4 (1)(a)(i)(A-G)) |  |  |  | Note project type here
R309-511-4 (1)(b) | Certification of hydraulic modeling results by PE provided (if project type is not listed in R309-511-4 (1)(a)(i)(A-G)) |  |  |  | Note reason here if answer is 'No'
R309-511-4 (2)(d) | Hydraulic model report provided (unless R309-511-4 (1)(a)(ii-iv) exemptions apply)
R309-511-4 (2)(f) | System capacity and expansion report provided in lieu of hydraulic model report (if required by the Director)
R309-550-5 (3)(b) | Hydraulic analysis provided for entire distribution system (>50% distribution system upgrade/new distribution system)
Distribution System Pressure
R309-105-9 (2)(a) | Minimum 20 psi peak day demand during fire flow
R309-105-9 (2)(b) | Minimum 30 psi peak instantaneous demand
R309-105-9 (2)(c) | Minimum 40 psi peak day demand
R309-550-5 (1)(a) | Minimum pressures maintained at points of connection under all flow conditions
R309-550-5 (1)(b) | Pressure reducing devices on new mains where static pressure exceeds 150 psi
Fire Suppression
R309-510-9 (1) | Distribution system sized for fire flow rate and duration according to local fire authority letter
R309-550-5 (5)(a) | Distribution system designed to meet fire flow requirements per local fire code official
R309-550-5 (5)(b) | Fire hydrant location per state-adopted fire code
R309-550-5 (5)(c) | Designed to meet minimum pressures throughout distribution system during fire flow
R309-550-5 (5)(d) | Minimum 6-inch diameter fire hydrant laterals
R309-550-6 (5)(a) | Fire hydrant drains separate from sewers
R309-550-6 (5)(a) | Fire hydrant drains greater than 10 feet from sanitary sewers
R309-550-6 (5)(a) | Fire hydrant drains greater than 10 feet from storm sewers
R309-550-6 (5)(b) | Fire hydrant laterals include auxiliary valves
R309-550-6 (5)(c) | Adequate fire hydrant drainage - acceptable natural soil, gravel pack, or dry well
Pipe Sizing
R309-510-9 (2)&(3) | Distribution system sized for peak instantaneous demand
R309-550-5 (2) | Distribution system designed using minimum flow rates for fire flow and peak instantaneous demand per R309-510
R309-550-5 (3)(a) | Water main size based on hydraulic analysis of flow demands and pressure requirements
R309-550-5 (4) | Minimum water main size: 4" w/o fire hydrants; 8" w/ fire hydrants; 6" w/ fire hydrants & hydraulic analysis
Cross Connection Control
R309-105-12 (1) | Backflow prevention on cross connections
R309-550-6 (8)(b) | Backflow device installation conforms to state plumbing code
R309-550-9 (1) | Physical cross-connections absent
R309-550-9 (2) | Condensate or cooling water from engine jackets or heat exchangers separate from drinking water supply
R309-550-9 (3) | Interconnection with another drinking water system approved by Director
Soil and Ground Water
R309-550-5 (6) | Soil characteristics considered for water main burial
R309-550-5 (9) | Distribution system materials appropriate for corrosive soil or water
R309-550-5 (10)(a)&(b) | Non-permeable distribution system materials specified in areas of contamination
R309-550-5 (11) | DDW-specified design requirements used for water mains near contamination areas
Design and Construction
R309-550-5 (6) | Special design and burial for CWS water mains in geologic hazard areas
R309-550-5 (7)(a) | Dead ends minimized by making appropriate tie-ins
R309-550-5 (7)(b) | Unavoidable dead ends equipped with fire hydrants, flush hydrants, or blow-off valves
R309-550-5 (7)(b) | Dead end flushing devices sized for minimum velocity of 2.5 fps in the water main
R309-550-5 (7)(b) | Flushing devices separate from sewers
R309-550-5 (8) | Maximum interval of 500' between isolation valves in commercial districts
R309-550-5 (8) | Maximum interval of one block or 800' between isolation valves in non-commercial districts
R309-550-5 (8) | Maximum interval of 1 mile between isolation valves in areas of widely scattered customers & no future development
R309-550-6 (1) | NSF/ANSI 61 certification specified for drinking water system components
R309-550-6 (2)(a) | Asbestos-cement pipe absent
R309-550-6 (2)(b) | Lead-free pipes and fittings specified
R309-550-6 (3) | NSF/ANSI 61, AWWA C104-A21.4-08 through C550-05, and C900-07 through C950-07 conformance specified
R309-550-8 (1)(a) | Specs incorporate manufacturer's installation procedures or AWWA C600-10 for ductile iron pipe
R309-550-8 (1)(b) | Specs incorporate manufacturer's installation procedures or ASTM D2774 and AWWA M23 for PVC pipe
R309-550-8 (1)(c) | Specs incorporate manufacturer's installation procedures or ASTM D2774 and AWWA M55 for HDPE pipe
R309-550-8 (1)(d) | Specs incorporate manufacturer's installation procedures or AWWA C604-11 for steel pipe
R309-550-8 (2) | Continuous uniform bedding specified for buried piping
R309-550-8 (3)(a) | Maximum 3/4-inch particle size specified for backfill material and for a min. of 6" below plastic pipe
R309-550-8 (3)(b) | Specs limit stones to maximum 2-inch diameter in backfill material and for a min. of 6" below ductile iron pipe
R309-550-8 (4) | Specs prohibit dropping pipe into trench
R309-550-8 (5) | Minimum cover specified to prevent freezing (pipe buried below depth of frost penetration)
R309-550-8 (6) | Thrust blocking, anchoring, tie rods, or restraints specified for tees, bends, plugs, and hydrants
R309-550-8 (6) | Pipe restraints properly sized for expected forces
R309-550-8 (7) | Pressure and leak testing specified per AWWA C600-10
R309-550-8 (9) | Specs require open ends of pipe to be sealed at end of day's construction
R309-550-8 (10) | Procedures specified for flushing, disinfection, and microbiological testing (flushing per AWWA C651-05)
Valves and Valve Chambers
R309-550-6 (6)(a) | Air relief valves/hydrants at distribution system high points
R309-550-6 (6)(b) | Automatic valve air relief vent pipe designed with non-corrodible #14 mesh screen cover
R309-550-6 (6)(b) | Downturned automatic valve air relief vent at least 1 foot above grade
R309-550-6 (6)(b) | Automatic valve air relief vent at least 1 foot above pipe in chamber with no flooding & adequate drainage
R309-550-6 (6)(c) | Air Relief/Blow Off Valves separate from sewers
R309-550-6 (6)(d) | Adequate number of hydrants or blow-off valves for water-line flushing
R309-550-6 (6)(e) | Air relief valve protected from freezing
R309-550-6 (6)(e) | Shut-off valve provided to service air relief valve
R309-550-6 (7)(a) | Valve or meter chambers separate from storm drains
R309-550-6 (7)(a) | Valve or meter chambers separate from sanitary sewers
R309-550-6 (7)(b) | Valve or meter chambers drain to daylight , have absorption pit, or use sump pumps
R309-550-6 (8)(a)(i) | Isolation valves on both sides of each pressure reducing valve
R309-550-6 (8)(a)(ii) | Parallel PRV lines provided to accommodate low and high flows
Waterline Separation from Sewers and Contamination
R309-550-7 (1)(a) | Minimum 10 foot lateral separation between water and sanitary sewer lines
R309-550-7 (1)(a) | Water line a minimum of 18 inches above sanitary sewer line where they cross
R309-550-7 (1)(b) | Water and sewer lines installed in separate trenches
R309-550-7 (1)(c) | Information provided to support minimum 6' water/sewer lateral separation distance due to local conditions
R309-550-7 (1)(d) | Exception request to minimum separation standards provided per R309-105-6 (2)(b)
R309-550-7 (3)(a) | Greater water/sewer separation distance specified in areas of high groundwater
R309-550-7 (3)(b) | Minimum 20 foot water/sewer separation required where water lines may become unpressurized
R309-550-7 (3)(c) | Measures specified to prevent/minimize disturbance of existing water or sewer lines
R309-550-7 (3)(d) | Pipe material reflects corrosive conditions and inability to meet minimum separation between water/sewer
R309-550-7 (3)(e)(i) | New sewer force main enclosed in continuous sleeve within 10 feet of water main crossing
R309-550-7 (3)(e)(ii) | Minimum rated working pressure of 200 psi specified for new water main crossing over existing sewer
R309-550-7 (4) | Water service laterals crossing sewer mains/laterals meet minimum separation distances
R309-550-12 (1) | Unpressurized flows in transmission lines minimized
R309-550-12 (2) | Unpressurized transmission lines located greater than 20 feet from concentrated source of pollution
R309-550-12 (2) | Unpressurized transmission lines located outside of boggy areas and areas of water ponding
Surface Water Crossings
R309-550-8 (8)(a) | Lines above open water adequately supported and anchored
R309-550-8 (8)(a) | Lines above open water protected from damage and freezing
R309-550-8 (8)(a) | Lines above open water accessible for repair and replacement
R309-550-8 (8)(b)(i) | Minimum 2 feet of cover specified for lines for underwater crossing
R309-550-8 (8)(b)(ii)(A) | Restrained joints below water and flexible joints at water edges specified for crossings greater than 15 feet
R309-550-8 (8)(b)(ii)(B) | Isolation valves specified on both sides of line crossing under water (beyond high ground water and flood zone)
R309-550-8 (8)(b)(ii)(C) | Sample taps specified upstream and downstream on line crossing under water
R309-550-8 (8)(b)(ii)(D) | Pressure testing specified for line crossing under water
Service Connections
R309-550-6 (8)(c) | Meter installation conforms to state plumbing code and local standards
R309-550-11 (2)(a) | Water services and plumbing conform to state-adopted plumbing code
R309-550-11 (2)(b) | Lead-free pipes and fittings specified for plumbing
R309-550-11 (2)(b) | Specs require plumbing pipes and fittings to be certified to meet NSF/ANSI 372 or NSF/ANSI 61, Annex G
R309-550-11 (3) | Individual service-connection booster pumps absent
R309-550-11 (4)(a) | Specs require service lines to be capped until connected
R309-550-11 (5) | Connection between service meter and home conforms to state-adopted plumbing code
Engineer's Certification
Yes
Yes