## Old
|  |  |  | Huntington Waste Water Flows | [8 empty] | Huntington Waste Water Flows
Evap Pond | 352 gpm | Plant Sewage Tratment | 5 gpm |  |  | Potable Water System | 5 | gpm | Evap Pond | 232 | Plant Sewage Tratment | 5 |  |  | Potable Water System | 5 | gpm
|  | Waste Disposal Basin | 347 gpm | Neutralizing Basin | 147 gpm | Misc Leaks | 4 | gpm |  |  | Waste Disposal Basin | 227 | Neutralizing Basin | 87 | Misc Leaks | 19 | gpm
[6 empty] | Turbine Cycle | 4 | gpm | [6 empty] | Turbine Cycle | 4 | gpm
[6 empty] | Sample Panel | 12 | gpm | [6 empty] | Sample Panel | 14 | gpm
[6 empty] | Abnormal Operation | 60 | gpm | [7 empty] | 0 | gpm
[6 empty] | Boiler System | 1 | gpm | [6 empty] | Boiler System | 1 | gpm
[6 empty] | Bearing Cooling Water | 5 | gpm | [6 empty] | Bearing Cooling Water | 5 | gpm
[6 empty] | ENU | 9 | gpm | [6 empty] | ENU | 9 | gpm
[6 empty] | Pit Redeler Washdown | 9 | gpm | [6 empty] | Plant Washdown | 20 | gpm
[6 empty] | Pit Leaks | 15 | gpm | [7 empty] | 0 | gpm
[6 empty] | 3 Belt Wash Down | 6 | gpm | [7 empty] | 0 | gpm
[6 empty] | Coal Yard Retention Basin | 3 | gpm | [7 empty] | 0 | gpm
[6 empty] | Mill Bay Wash Down | 1 | gpm | [7 empty] | 0 | gpm
[6 empty] | Circ Water Sample Flows | 2 | gpm | [7 empty] | 0 | gpm
[6 empty] | North Storm Drains | 3 | gpm | [6 empty] | Storm Water Drains | 9 | gpm
[6 empty] | Redler Deck Dust System | 4 | gpm | [7 empty] | 0 | gpm
[6 empty] | Lacy's Sump | 6 | gpm | [6 empty] | Lacy's Sump | 6 | gpm
[6 empty] | Roof Drains | 3 | gpm | [7 empty] | 0 | gpm
[6 empty] | Total | 147 | gpm | [6 empty] | Total | 87 | gpm
|  |  |  | Waste Disposal Basin | 200 gpm | Ash Tank Over Flow | 5 | gpm |  |  |  |  | Waste Disposal Basin | 140 | Ash Tank Over Flow | 5 | gpm
[6 empty] | Abnormal Operation | 60 | gpm | [7 empty] | 0 | gpm
[6 empty] | Process Sump | 130 | gpm | [6 empty] | Process Sump | 130 | gpm
[6 empty] | DM Makeup Tank Overflow | 5 | gpm | [6 empty] | DM Makeup Tank Overflow | 5 | gpm
[6 empty] | Total | 200 | gpm | [6 empty] | Total | 140 | gpm

## New
Huntington Waste Water Flows
Irrigation Storage Reservoir | 232 | gpm | Plant Sewage Treatment | 5 | gpm |  |  |  | Potable Water System | 5 | gpm
|  |  | Waste Disposal Basin | 227 | gpm | Neutralizing Basin | 87 | gpm | Miscellaneous Packing Flows | 19 | gpm
[9 empty] | Turbine Cycle Drains | 4 | gpm
[9 empty] | Laboratory Sample Panel | 14 | gpm
[9 empty] | Boiler System Blowdown | 1 | gpm
[9 empty] | Bearing Cooling Water Blowdown | 5 | gpm
[9 empty] | Elementary Neutralization Unit | 9 | gpm
[9 empty] | Plant Drains | 20 | gpm
[9 empty] | Storm Water | 9 | gpm
[9 empty] | Drying Pad Drainage | 6 | gpm
[9 empty] | Total | 87 | gpm
[6 empty] | Waste Disposal Basin | 140 | gpm | Cooling Tower Blowdown | 5 | gpm
[9 empty] | Process Water | 130 | gpm
[9 empty] | Demineralizer Makeup Overflow | 5 | gpm
[9 empty] | Total | 140 | gpm